## datamap
Project Prime Thermostat Datamap | [12 empty] | Changes from previous FINAL version marked in yellow, except for the description column which is cumulative.
v2.2.4 FINAL 04/23/2025 | [12 empty] | description changes marked in orange |  | white not yet updated.
id | name | datatype | min | max | default | persist | gui | equip | cloud | protocolreset | cloudreset | public | CTrequired | P1P2required | S21required | DK1miniP1P2S21 | DK1adaptorP1P2 | DK1adaptorS21 | DK1adaptorCT | DK1MiniCT | DK1plus | DK1MidTier | description
//System Status and Information
0 | equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
1 | cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current cooling setpoint used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control. Resolution is 0.1deg C.
2 | hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current heating setpoint used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control. Resolution is 0.1deg C.
3 | tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor temperature in 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
4 | tempOutdoor | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current outdoor temperature, via weather service or eventually an external sensor that is standalone (if present) or that is in the equipment; 255: No external sensor or forecast; Used for the outdoor temperature displayed on the air quality screen and for lockouts. Up to v2.7 software release this is always the temperature from the weather service when connected to WiFi, not populated otherwise.
5 | humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor humidity; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
6 | humOutdoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current outdoor humidity with 1% resolution, via weather service or eventually an external sensor if present; 255: No external sensor or forecast; Displayed on the air quality screen as the outdoor humidity level.
//Control Settings
7 | mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
8 | modeLimit | UINT8 | 0 | 4 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode limit derived from equipment capabilities and the non-communicating equipment settings; 0: none, 1: all, 2: heat only, 3: cool only; 4: auto and off only (for a P1P2 follower); Used to determine what system modes to display in UI.
9 | modeEmHeatAvailable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Emergency heat is available as a system mode; 0: not available, 1: available; PIC24 protocol software sets this on equipment power up, and only if HP heat and another heat source are available. In P1P2 and S21 systems this is always tied to an aux heat source wired to the thermsotat aux terminals.
A | modeForceOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED: Regardless of mode, consider system to be off; (not used in phase 1)
B | control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
C | fan | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; System fan; 0: auto, 1:on; "fanCirculate" variable used instead of this one.
//Temperature Settings
D | cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
E | hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
F | cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is set to TRUE or "control" set to "1: Away".
10 | hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is set to TRUE or "control" set to "1: Away".
11 | cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
12 | hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
13 | tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
14 | tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
15 | tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
16 | tempOffset | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Offset to the temperature value displayed by the thermostat in 0.5deg C steps, as set in the installer temperature calibration screen.
// Humidity Settings
17 | humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
18 | dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
19 | humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
1A | humDeadband | UINT8 | 5 | 20 | 10 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | NOT USED
1B | humOffset | INT8 | -30 | 30 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Offset to the humidity value displayed by the thermostat in 1% steps, as entered by the installer in the humidity calibration screen.
//Air Quality
1C | aqIndoorAvailable | BIT | 0 | 1 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor air quality available; 0=no data; 1=data available;
1D | aqIndoorLevel | UINT8 | 0 | 5 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor air quality level from TZOA "aqi_color" telemetry data; 0: good (green), 1: moderate (yellow), 2: unhealthy for sensitive groups (orange), 3: unhealthy (red), 4: very unhealthy (purple), 5: hazardous (maroon); From TZOA stream, mimics gov't levels. Determines color of indoor air qualtiy text in UI.
1E | aqIndoorValue | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor air quality relative value, on scale of 0 to 300; is telemetry data "aqi" variable time 1000. A value of "0" means the unit is still in the calibration period. Not used by UI.
1F | aqIndoorVOCValue | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor relative VOC value, on scale of 0 to 300; is telemetry data "voc" variable time 1000. Determines length of "chemicals" bar in UI.
20 | aqIndoorParticlesValue | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor pm2.5 relative value, on scale of 0 to 300; is telemetry data "pm" variable time 1000. Determines length of "particles" bar in UI.
21 | aqOutdoorAvailable | BIT | 0 | 1 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Outdoor air quality available; 0=no data; 1=data available;
22 | aqOutdoorLevel | UINT8 | 0 | 5 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current outdoor air quality level 0: good, 1: moderate, 2: unhealthy for sensitive groups, 3: unhealthy, 4: very unhealthy, 5: hazardous; (as defined by U.S. government) Populated by VenOS from the nearest weather station if the thermostat is connected and has a mobile app address.
23 | aqOutdoorValue | UINT16 | 0 | 500 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current outdoor Air Quality Index (AQI) value; also populated by VenOS from the weather service data.
24 | aqOutdoorOzone | UINT16 | 0 | 500 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current Ozone in micrograms per meters cubed; also populated by VenOS from the weather service data.
25 | aqOutdoorParticles | UINT16 | 0 | 500 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current outdoor particles parts per billion per cubic foot; also populated by VenOS from the weather service data.
//Skyport and WiFi Status
26 | wifiEnabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | WiFi enabled; 0: off, 1: on; populated from checkbox in UI found in both dealer and homeowner menus.
27 | wifiLinkStatus | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | WiFi state; 0: disconnected, 1: connecting, 2: connected; populated by VenOS, drives display of "networks" status;
28 | wifiNetworkStatus | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | WiFi Network Status; populated by VenOS, drives display of "internet" status with 0="not connected" and 1="connected".
29 | wifiIPv4Address | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System IPv4 address; Populated by Skyport cloud.
2A | wifiIPv6Address | CHAR | 0 | 45 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System IPv6 address; Populated by Skyport cloud.
2B | wifiMACAddress | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | WiFi MAC address; populated by VenOS
2C | wifiNetworkName | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of STA network connected; Populated by VenOS when connects to a wifi network, drives display of the network name next to the "network" field.
2D | wifiNetworkSignal | UINT8 | 0 | 100 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | WiFi network signal strength; populated by VenOS, used to display strength of the WiFi signal for the connected network;
2E | skyportStatus | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Skyport connection status; drives display of the "Daikin One Cloud" status, with 0="not connected" and 1="connected".
2F | skyportAccountID | CHAR | 0 | 64 | NULL | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Skyport account name; is the online acocunt the thermostat is linked to, aka the homeowner email address, displayed on the "account" screen.
30 | skyportAuthToken | CHAR | 0 | 64 | NULL | TRUE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Skyport account association code; Populated by Skyport cloud.
31 | skyportPairingToken | UINT32 | 0 | 999999 | NULL | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Skyport pairing token; Populated by Skyport cloud.
32 | skyportCommissioned | BIT | 0 | 1 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Skyport commissioned flag; Populated by Skyport cloud.
//Wireless Zones
36 | rfEnabled | BIT | 0 | 1 | 1 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | SubGHz rf network enable; 0: off, 1: on
37 | rfAllowControl | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | NOT USED; SubGig allow make changes to other nodes; 0: off, 1: on
38 | rfStatus | UINT8 | 0 | 3 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | SubGHz status; 0: off, 1: broadcasting, 2: searching, 3: connected to parent
39 | rfNetworkType | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | NOT USED; Control level of this thermostat; 0: parent (master), 1: child
3A | rfNetworkSignal | UINT8 | 0 | 100 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | NOT USED; Connected network signal strength
3B | rfNetworkName | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | NOT USED; Name of the SubGig network created or connected
//Weather Forecast
3D | weatherTodayIcon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current weather icon; Text string such as "sunny", but driving icon display on air quality page.
3E | weatherTodayTempC | FLOAT | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current weather temperature in 0.1deg C;
3F | weatherTodayHum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current weather humidity in percent
41 | weatherDay1Icon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 1 weather icon
42 | weatherDay1TempC | INT8 | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 1 weather temperature in 0.1deg C
43 | weatherDay1Hum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 1 weather humidity
45 | weatherDay2Icon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 2 weather icon
46 | weatherDay2TempC | INT8 | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 2 weather temperature in 0.1deg C
47 | weatherDay2Hum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 2 weather humidity
49 | weatherDay3Icon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 3 weather icon
4A | weatherDay3TempC | INT8 | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 3 weather temperature in 0.1deg C
4B | weatherDay3Hum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 3 weather humidity
4D | weatherDay4Icon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 4 weather icon
4E | weatherDay4TempC | INT8 | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 4 weather temperature in 0.1deg C
4F | weatherDay4Hum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 4 weather humidity
51 | weatherDay5Icon | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 5 weather icon
52 | weatherDay5TempC | INT8 | -90 | 60, 127 | 127 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 5 weather temperature in 0.1deg C
53 | weatherDay5Hum | UINT8 | 0 | 100, 127 | 0 | FALSE | READ | READ | READWRITE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Day 5 weather humidity
//Geofencing
54 | geofencingEnabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled; 1: enabled. If enabled by checking "receive geofencing events" checkbox in the settings-> away menu of homeowner UI (the default), VenOS will switch to the Away setpoints when "geofencingAway" is set to TRUE.
55 | geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Dealer Info
95 | dealerName | CHAR | 0 | 64 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of the dealer who set up the thermostat, if entered; Displayed on the "Support" page under "Daikin Dealer" in v2.7 release.
96 | dealerEmail | CHAR | 0 | 128 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Email address for the dealer who set up the thermostat, if entered; Displayed on the "Support" page under "Daikin Dealer" in v2.7 release.
97 | dealerPhone | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phone number for the dealer who set up the thermostat, if entered; Displayed on the "Support" page under "Daikin Dealer" in v2.7 release.
98 | dealerWebsite | CHAR | 0 | 128 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Website for the dealer who set up the thermostat, if entered; Displayed on the "Support" page under "Daikin Dealer" in v2.7 release.
99 | dealerMessage | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Custom message by the dealer who set up the thermostat, if entered; Displayed on the "Support" page under "Daikin Dealer" in v2.7 release.
//Display and Settings
9A | language | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: English, 1: Spanish, 2: French; Display language to use throughout the system; Set under "display" menu.
9B | units | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Fahrenheit, 1: Celsius; Temperature unit to use throughout the system; set in "display" menu by "degree units" selection.
9C | systemTime24 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: 12-hour clock; 1: 24-hour clock; Display clock in 24-hour format; set in "date & time" menu with "use 24-hour time format" check box.
9D | deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
9E | deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when deviceName is 0;
9F | displayBrightness | UINT8 | 0 | 100 | 90 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current backlight brightness for the display in %; set by UI to dim or turn off display for various modes.
A0 | displayDefaultBrightness | UINT8 | 0 | 100 | 90 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User-defined backlight brightness for the display when fully on.
A1 | nightModeEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | When "night mode" is enabled the display and light pipe (if applicable) are turned off when night mode is active.
A2 | nightModeActive | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used by VenOS to indicate when "night mode" is active, which is when it is enabled and the system clock is in between the start and end time.
A3 | nightModeLightBarAllowed | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0=light bar off; 1=light bar on; Allow the light bar to turn on during the night mode; Not implemented in UI for user to change;
A4 | nightModeStart | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start hour for "night mode" in 15 minute increments
A5 | nightModeStop | UINT8 | 0 | 95 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | End hour for "night mode" in 15 minute increments
A6 | lightBarEnabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable use of the LED light bar. If enabled, the "lightBarBrightness" variable sets the brightness.
A7 | soundEnabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | If enabled the magnetic encoder thermostat will play tick sounds when rotated. Not used for rotary encoder thermostat.
A8 | screenSaverMode | UINT8 | 0 | 3 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | What to display for the screen saver; 0: off, 1: blank screen, 2: analog clock, 3: digital clock
A9 | timeZone | CHAR | 1 | 50 | America/Los_Angeles | TRUE | READWRITE | NONE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time Zone of the location; Set by Skyport if connected to homeowner app.
AA | displayLockPIN | UINT16 | 0 | 9999 | 0 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | PIN set by user to lock the thermostat display. Can be unlocked witout code by power cycling the thermostat.
//Schedule
AB | schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
AC | schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
AD | schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
AE | schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
AF | schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
B0 | schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
B1 | schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
B2 | schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
B3 | schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
B4 | schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
B5 | schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
B6 | schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
B7 | schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
B8 | schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
B9 | schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
BA | schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
BB | schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
BC | schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
BD | schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
BE | schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
BF | schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
C0 | schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
C1 | schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
C2 | schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
C3 | schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
C4 | schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
C5 | schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
C6 | schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
C7 | schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
C8 | schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
C9 | schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
CA | schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
CB | schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
CC | schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
CD | schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
CE | schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
CF | schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
D0 | schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
D1 | schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
D2 | schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
D3 | schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
D4 | schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
D5 | schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
D6 | schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
D7 | schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
D8 | schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
D9 | schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
DA | schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
DB | schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
DC | schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
DD | schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
DE | schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
DF | schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
E0 | schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
E1 | schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
E2 | schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
E3 | schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
E4 | schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
E5 | schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
E6 | schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
E7 | schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
E8 | schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
E9 | schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
EA | schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
EB | schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
EC | schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
ED | schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
EE | schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
EF | schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
F0 | schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
F1 | schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
F2 | schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
F3 | schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
F4 | schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
F5 | schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
F6 | schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
F7 | schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
F8 | schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
F9 | schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
FA | schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
FB | schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
FC | schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
FD | schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
FE | schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
FF | schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
100 | schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
101 | schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
102 | schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
103 | schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
104 | schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
105 | schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
106 | schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
107 | schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
108 | schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
109 | schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
10A | schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
10B | schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
10C | schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
10D | schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
10E | schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
10F | schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
110 | schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
111 | schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
112 | schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
113 | schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
114 | schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
115 | schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
116 | schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
117 | schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
118 | schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
119 | schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
11A | schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
11B | schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
11C | schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
11D | schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
11E | schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
11F | schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
120 | schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
121 | schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
122 | schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
123 | schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
124 | schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
125 | schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
126 | schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
127 | schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
128 | schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
129 | schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
12A | schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
12B | schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
12C | schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
12D | schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
12E | schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
12F | schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
130 | schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
131 | schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
132 | schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
133 | schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
134 | schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
135 | schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
136 | schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
137 | schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
138 | schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
139 | schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
13A | schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
13B | schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
13C | schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
13D | schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
13E | schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
13F | schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
140 | schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
141 | schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
142 | schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
143 | schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
144 | schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
145 | schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
146 | schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
147 | schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
148 | schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
149 | schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
14A | schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
14B | schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
14C | schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
14D | schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
14E | schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
14F | schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
150 | schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
151 | schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
152 | schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
153 | schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
154 | schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
155 | schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
156 | schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
157 | schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
158 | schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
159 | schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
15A | schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
15B | schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
15C | schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
15D | schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
15E | schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
15F | schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
160 | schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
161 | schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
162 | schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
163 | schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
164 | schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
165 | schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
166 | schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
167 | schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
168 | schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
169 | schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
16A | schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
16B | schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
16C | schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
16D | schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
16E | schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
16F | schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
170 | schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
171 | schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
172 | schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
173 | schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
174 | schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
175 | schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
176 | schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
177 | schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
178 | schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
179 | schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
17A | schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
17B | schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
17C | schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
17D | schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
17E | schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
17F | schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
180 | schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
181 | schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
182 | schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
183 | schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
184 | schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
185 | schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
186 | schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
187 | schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
188 | schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
189 | schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
18A | schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
18B | schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
18C | schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
18D | schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
18E | schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
18F | schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
190 | schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
191 | schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
192 | schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
193 | schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
194 | schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
195 | schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
196 | schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
197 | schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
198 | schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
199 | schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
19A | schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
19B | schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
19C | schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
19D | schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
19E | schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
19F | schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
1A0 | schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
1A1 | schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
1A2 | schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
1A3 | schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
1A4 | schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
1A5 | schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
1A6 | schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
1A7 | schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
1A8 | schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
1A9 | schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
1AA | schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//ADR
1AB | adrEnabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Enable automated demand response system. Could be enabled or enabled by user in the thermostat UI, or through cloud from utility program when a user signs up or opts out. Equipment control is done through the 0x4246 ctRatedPowerUpperLimitSupported, 0x4247 ctRatedPowerUpperLimit, 0x4248 ctRatedPowerUpperLimitEnable variables.
1AC | adrState | UINT8 | 0 | 5 | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Current state of ADR operation; 0: None, 1: STDDELTA, 2: STDFIXED, 3: PRICEDELTA, 4: PRICEFIXED, 5: PENDING
1AD | adrStatus | UINT8 | 0 | 8 | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; 0: Not in curtailment, 1: In standard curtailment (delta), 2: In standard curtailment (fixed), 3: In price curtailment (delta), 4: In price curtailment (fixed), 5: Pending curtailment, 6: Pending curtailment Where (eventPrice < curPriceTrigger), 7: In price curtailment (delta) but not curtailing due to (eventPrice < curPriceTrigger) == true, 8: In price curtailment (fixed) but not curtailing due to (eventPrice < curPriceTrigger) == true
1AE | adrAction | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Action to perform when an ADR event is received; 0: observe setpoint offsets, 1: observe static setpoints (2: percent of power reduction)
1AF | adrEventCoolMax | FLOAT | 10 | 32.2 | 29 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Maximum cooling threshold during an ADR event in 0.1deg C
1B0 | adrEventHeatMin | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Minimum heating threshold during an ADR event in 0.1deg C
1B1 | adrStaticCool | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Static cooling threshold to use during an ADR event in 0.1deg C
1B2 | adrStaticHeat | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Static heating threshold to use during an ADR event in 0.1deg C
1B3 | adrOffsetCool | FLOAT | 0.5 | 4 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Amount to offset cooling thresholds during an ADR event in 0.5deg C
1B4 | adrOffsetHeat | FLOAT | -4 | -0.5 | -2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Amount to offset heating thresholds during an ADR event in 0.5deg C
1B5 | adrActualStart | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Time that the event started including the delay added for the random delay
1B6 | adrActualStop | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; The actual stopping time of the event, including the random delay
1B7 | adrPrice | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Current price of electricity
1B8 | adrEventId | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Active or Most recently completed ADR event ID
//Equipment
1B9 | ctOutdoorQuietModeEnabled | UINT8 | 1 | 2 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off (disabled); 2: on (enabled); Set through UI, used for old and new quiet mode.
1BA | quietModeActive | UINT8 | 1 | 2 | 1 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: active; Activated according to quiet mode schedule. Used for old and new quiet mode.
1BB | quietModeStartTime | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Time at which to start quiet mode for the compressor in 15 minute increments covering 24 hours. Used as the start time for quiet mode schedule event 1 in new quiet mode.
1BC | quietModeStopTime | UINT8 | 0 | 95 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Time at which to stop quiet mode for the compressor in 15 minute increments to cover 24 hours. Used as the start time for quiet mode schedule event 2 in new quiet mode.
1BD | ctOutdoorNoiseDownLevel | UINT8 | 1 | 3, 0xFF | 3 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: quiet (level 1); 2: quieter (level 2); 3: quietest (level 3); Selected by installer in UI. Used by UI to display the quiet mode settings when populated. Used as the noise down level for quiet mode schedule event 1 in new quiet mode, but not written directly to the equipment.
1BE | ctOutdoorCapacityPriority | UINT8 | 1 | 2, 0xFF | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Overrides quiet mode when too far from setpoint temp for too long. Used as the capacity priority setting for quiet mode schedule event 1 in new quiet mode, but not written directly to the equipment.
1BF | fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
1C0 | fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Set by VenOS both if "fanCirculate"==1 for "Always ON", or if "fanCirculate" = 2 for "on a schedule". Used by PIC24 code to circulate air when no heat or cool call, but UI uses "equipmentStatus"==4 to display the "circulating air" message.
1C1 | fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
1C2 | fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
1C3 | fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
1C4 | fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
1C5 | fanExtendHeat | UINT32 | 0 | 0xFFFFFFFF | 300000 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; Duration in milliseconds to run fan after heat cycle
1C6 | fanExtendCool | UINT32 | 0 | 0xFFFFFFFF | 300000 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; Duration in milliseconds to run fan after cool cycle
1C7 | compressorMinOff | UINT32 | 0 | 0xFFFFFFFF | 600000 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; Minimum number of milliseconds to wait before restarting the compressor after shutdown.
1C8 | compressorMinOn | UINT32 | 0 | 0xFFFFFFFF | 600000 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; Minimum number of milliseconds to run the compressor when humidifying.
1C9 | overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
1CA | heatPumpLockoutEnable | UINT8 | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled; 1: enabled; (no UI setting to disable through at least the v3.1 release)
1CB | heatPumpLockoutTemp | FLOAT | -40 | 18.5 | -20.5 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Minimum outdoor temperature in C° required to operate the heat pump. Only used for systems with a HP and another heat source (heater kit, gas furnace, and/or aux heat source).
1CC | auxHeatLockoutEnable | UINT8 | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled; 1: enabled; (no UI setting to disable through at least the v3.1 release)
1CD | auxHeatLockoutTemp | FLOAT | -34.5 | 24 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Outdoor temperature in C° above which the heater kit is locked out. Used as the balance point for dual-fuel systems, and above this temp the furnace may or may not be used. Only used for systems with a HP and another heat source (heater kit or gas furnace).
1CE | equipmentCapability | UINT8 | 0 | 3 | 0 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Equipment heat/cool capability; 0: none, 1: cool available, 2: heat available, 3: both available
1CF | equipmentCommunication | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Communication equipment protocol; 0: ClimateTalk, 1: P1P2, 2: S21
//Alerts
1D0 | alertsServiceEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Opt-in to service alerts on the thermostat
1D1 | alertsEducationEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Opt-in to education alerts (tips) on the thermostat
1D2 | alertsWeatherEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Opt-in to weather alerts on the thermostat
1D3 | alertsSharingEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Share all alerts with the dealer
1D4 | alertMediaAirFilterDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace air filter in calendar days
1D5 | alertMediaAirFilterDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current air filter runtime in days
1D6 | alertMediaAirFilterRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Frequency to receive reminders to replace air filter in runtime
1D7 | alertMediaAirFilterRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current air filter runtime in hours
1D8 | alertMediaAirFilterActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace air filter alert is triggered
1D9 | alertMediaAirFilterDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace air filter alert is triggered
1DA | alertHEPAAirFilterDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace air filter in calendar days
1DB | alertHEPAAirFilterDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current air filter runtime in days
1DC | alertHEPAAirFilterRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Frequency to receive reminders to replace air filter in runtime
1DD | alertHEPAAirFilterRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current air filter runtime in hours
1DE | alertHEPAAirFilterActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace air filter alert is triggered
1DF | alertHEPAAirFilterDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace air filter alert is triggered
1E0 | alertElectronicAirFilterDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace air filter in calendar days
1E1 | alertElectronicAirFilterDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current air filter runtime in days
1E2 | alertElectronicAirFilterRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Frequency to receive reminders to replace air filter in runtime
1E3 | alertElectronicAirFilterRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current air filter runtime in hours
1E4 | alertElectronicAirFilterActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace air filter alert is triggered
1E5 | alertElectronicAirFilterDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace air filter alert is triggered
1E6 | alertUVRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace UV bulbs
1E7 | alertUVRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current UV bulb runtime
1E8 | alertUVActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace UV bulbs alert is triggered
1E9 | alertUVDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace UV bulbs alert is triggered
1EA | alertVentilationDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to clean ventilation in days
1EB | alertVentilationDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current ventilation runtime in days
1EC | alertVentilationActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Clean ventilation alert is triggered
1ED | alertVentilationDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the clean ventilation alert is triggered
1EE | alertDehumFilterRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace dehumidifier filter
1EF | alertDehumFilterRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current dehumidifier filter runtime
1F0 | alertDehumFilterActive | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace dehumidifier filter alert is triggered
1F1 | alertDehumFilterDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace dehumidifier filter alert is triggered
1F2 | alertHumPadRuntimeLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace the humidifier pad
1F3 | alertHumPadRuntime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current humidifier pad runtime
1F4 | alertHumPadActive | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Replace humidifier pad alert is triggered
1F5 | alertHumPadDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the replace humidifier pad alert is triggered
1F6 | alertUVDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace UV bulbs in calendar days
1F7 | alertUVDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current UV bulbs runtime in days
1F8 | alertDehumFilterDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace dehumidifier filter in calendar days
1F9 | alertDehumFilterDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current dehumidifier filter runtime in days
1FA | alertHumPadDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to replace humidifier pad in calendar days
1FB | alertHumPadDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current humidifier pad runtime in days
1FC | alertServiceDaysLimit | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Frequency to receive reminders to service system in calendar days
1FD | alertServiceDays | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--Current runtime in days since the system was last serviced
1FE | alertServiceActive | BIT | 0 | 1 | 0 | TRUE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System service alert is triggered
1FF | alertServiceDate | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date the system service alert is triggered
//CT Equipment Errors (last 25)
200 | fault1Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | timestamp in UNIX epoch time based on GMT; added when logged in error history;
201 | fault1Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | ClimateTalk and P1P2/S21--Hex value = error code, as reported by equipment
202 | fault1Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | For ClimateTalk--1: minor; 2: critical For P1P2/S21: Unit number (upper 4 bits); Fault level (lower 4 bits) 1: Critical; 2: Major; 8: Minor
203 | fault1Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment; For P1P2 and S21 this is the Detailed Error Code;
204 | fault2Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
205 | fault2Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
206 | fault2Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
207 | fault2Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
208 | fault3Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
209 | fault3Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20A | fault3Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20B | fault3Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20C | fault4Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20D | fault4Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20E | fault4Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
20F | fault4Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
210 | fault5Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
211 | fault5Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
212 | fault5Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
213 | fault5Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
214 | fault6Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
215 | fault6Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
216 | fault6Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
217 | fault6Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
218 | fault7Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
219 | fault7Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21A | fault7Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21B | fault7Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21C | fault8Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21D | fault8Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21E | fault8Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
21F | fault8Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
220 | fault9Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
221 | fault9Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
222 | fault9Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
223 | fault9Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
224 | fault10Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
225 | fault10Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
226 | fault10Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
227 | fault10Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
228 | fault11Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
229 | fault11Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22A | fault11Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22B | fault11Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22C | fault12Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22D | fault12Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22E | fault12Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
22F | fault12Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
230 | fault13Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
231 | fault13Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
232 | fault13Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
233 | fault13Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
234 | fault14Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
235 | fault14Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
236 | fault14Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
237 | fault14Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
238 | fault15Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
239 | fault15Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23A | fault15Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23B | fault15Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23C | fault16Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23D | fault16Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23E | fault16Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
23F | fault16Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
240 | fault17Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
241 | fault17Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
242 | fault17Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
243 | fault17Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
244 | fault18Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
245 | fault18Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
246 | fault18Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
247 | fault18Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
248 | fault19Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
249 | fault19Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24A | fault19Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24B | fault19Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24C | fault20Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24D | fault20Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24E | fault20Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
24F | fault20Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
250 | fault21Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
251 | fault21Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
252 | fault21Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
253 | fault21Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
254 | fault22Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
255 | fault22Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
256 | fault22Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
257 | fault22Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
258 | fault23Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
259 | fault23Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25A | fault23Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25B | fault23Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25C | fault24Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25D | fault24Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25E | fault24Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
25F | fault24Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
260 | fault25Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
261 | fault25Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
262 | fault25Level | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
263 | fault25Equipment | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
//CT Thermostat Errors (last 20), additions for sensor # and zone #.
264 | fault1SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Sensor number (1-8) for "sysFault*" thermostat errors; 0xFF is none.
265 | fault1ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone number (1-6) for "sysFault*" thermostat errors; 0xFF is none.
266 | fault2SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
267 | fault2ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
268 | fault3SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
269 | fault3ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26A | fault4SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26B | fault4ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26C | fault5SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26D | fault5ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26E | fault6SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
26F | fault6ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
270 | fault7SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
271 | fault7ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
272 | fault8SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
273 | fault8ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
274 | fault9SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
275 | fault9ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
276 | fault10SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
277 | fault10ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
278 | fault11SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
279 | fault11ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27A | fault12SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27B | fault12ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27C | fault13SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27D | fault13ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27E | fault14SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
27F | fault14ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
280 | fault15SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
281 | fault15ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
282 | fault16SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
283 | fault16ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
284 | fault17SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
285 | fault17ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
286 | fault18SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
287 | fault18ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
288 | fault19SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
289 | fault19ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
28A | fault20SensorNum | UINT8 | 1 | 8, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
28B | fault20ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//CT Equipment Errors (last 25), additions for zone #.
2A0 | eqFault1ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone number (1-6) for "fault*"zoning errors generated by the CT PIC24 zoning code; 0xFF is none.
2A1 | eqFault2ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A2 | eqFault3ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A3 | eqFault4ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A4 | eqFault5ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A5 | eqFault6ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A6 | eqFault7ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A7 | eqFault8ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A8 | eqFault9ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2A9 | eqFault10ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AA | eqFault11ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AB | eqFault12ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AC | eqFault13ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AD | eqFault14ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AE | eqFault15ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2AF | eqFault16ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B0 | eqFault17ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B1 | eqFault18ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B2 | eqFault19ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B3 | eqFault20ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B4 | eqFault21ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B5 | eqFault22ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B6 | eqFault23ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B7 | eqFault24ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
2B8 | eqFault25ZoneNum | UINT8 | 1 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
// New Quiet Mode variables
2D0 | quietNoiseDownLevelToEquip | UINT8 | 1 | 3, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: quiet (level 1); 2: quieter (level 2); 3: quietest (level 3); VenOS writes the schedule event values to this variable, which is the new "NoiseDownLevel" that is sent by the CT PIC24 code to the equipment.
2D1 | quietCapacityPriorityToEquip | UINT8 | 1 | 2, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Overrides quiet mode when too far from setpoint temp for too long. VenOS writes the schedule event values to this variable, which is the new "CapacityPriority" setting that is sent by the CT PIC24 code to the equipment.
2D2 | quietModeSched1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 = disabled; 1 = enabled; Default '1' to copy legacy quiet mode. There always must be at least 1 event (enforced by UI). Note that the quiet mode schedule event 1 start time, noise down level, and capacity priority setting reuse the original "quietModeStartTime", "ctOutdoorNoiseDownLevel", and "ctOutdoorCapacityPriority" variables, respectively.
2D3 | quietModeSched1Name | CHAR | 0 | 32 | night time | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Name of this quiet mode event; Default is "night time" from legacy quiet mode.
2D4 | quietSched1SupressOnOff | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; Default is ON for event 1 to preserve legacy quiet mode start time. This new variable is needed to turn quiet mode off for a schedule event, since the "NoiseDownLevel" value are sent directly to the equipment and don't support a value for OFF.
2D5 | quietModeSched2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 = disabled; 1 = enabled; Default '1' to copy legacy quiet mode stop time event. Note that the quiet mode schedule event 2 start time reuses the original "quietModeStopTime"variable.
2D6 | quietModeSched2Name | CHAR | 0 | 32 | day time | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Name of this quiet mode event; Default is "day time" from legacy quiet mode.
2D7 | quietSched2SupressOnOff | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; Default is OFF for event 2 to preserve legacy quiet mode stop time.
2D8 | quietSched2NoiseDownLevel | UINT8 | 1 | 3, 0xFF | 3 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: quiet (level 1); 2: quieter (level 2); 3: quietest (level 3); Selected by installer in UI. Used by UI to display the quiet mode settings when populated. Used as the noise down level for quiet mode schedule event 1 in new quiet mode, but not written directly to the equipment.
2D9 | quietSched2CapacityPriority | UINT8 | 1 | 2, 0xFF | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Overrides quiet mode when too far from setpoint temp for too long.
2DA | quietModeSched3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this quiet mode event is enabled.
2DB | quietModeSched3Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Name of this quiet mode event; Default is "day time" from legacy quiet mode.
2DC | quietModeSched3StartTime | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments;
2DD | quietSched3SupressOnOff | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On;
2DE | quietSched3NoiseDownLevel | UINT8 | 1 | 3, 0xFF | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: quiet (level 1); 2: quieter (level 2); 3: quietest (level 3);
2DF | quietSched3CapacityPriority | UINT8 | 1 | 2, 0xFF | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Overrides quiet mode when too far from setpoint temp for too long.
2E0 | quietModeSched4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Set to a '1' when this quiet mode event is enabled.
2E1 | quietModeSched4Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Name of this quiet mode event; Default is "day time" from legacy quiet mode.
2E2 | quietModeSched4StartTime | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments;
2E3 | quietSched4SupressOnOff | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On;
2E4 | quietSched4NoiseDownLevel | UINT8 | 1 | 3, 0xFF | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: quiet (level 1); 2: quieter (level 2); 3: quietest (level 3);
2E5 | quietSched4CapacityPriority | UINT8 | 1 | 2, 0xFF | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Overrides quiet mode when too far from setpoint temp for too long.
// Temperature and hardware Extras
300 | sensorRawTemperature | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current raw indoor temperature measured by the thermostat sensor with 0.1deg C resolution; 255: Sensor error
301 | sensorRawHumidity | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current raw indoor humidity measured by the thermostat sensor with 1% resolution; 255: Sensor error
302 | sensorDynamicAlgorithmTempOffset | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Dynamic calibration offset for indoor temperature with 0.1deg C resolution; from the TCE (temperature compensation engine) algorithm for the paricular thermostat model.
303 | sensorDynamicAlgorithmHumOffset | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Dynamic calibration offset for indoor humidity in 1% resolution; generally is a fixed value but could be dynamic in the future.
304 | TstatCalculatedTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor temperature in 0.1deg C resolution; 255: Sensor error. This value is the final thermostat temperature, calculated by taking the "sensorRawTemperature" value and applying the "sensorDynamicAlgorithmTempOffset" from the TCE and the "tempOffset" selected by the installer during temperature calibration.
305 | TstatCalculatedHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor humidity; 255: Sensor error; This value is the final thermostat humidity, calculated by taking the "sensorRawHumidity" value and applying the "sensorDynamicAlgorithmHumOffset" from the TCE and the "humOffset" selected by the installer during temperature calibration.
306 | TstatHWTemp1 | FLOAT | -40 | 90, 255 | 255 | FALSE | NONE | NONE | NONE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Main MPU temp
307 | TstatHWTemp2 | FLOAT | -40 | 90, 255 | 255 | FALSE | NONE | NONE | NONE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | sub-GHz radio temp
308 | internalHWCal | INT16 | -2999 | 2999, 0x7FFF | 0x7FFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | Internal HW calibration value for GTST thermostats (Lite platform).
// Test Mode values
0x0310 | tempHumTestMode | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: test mode off; 1: test mode on; When test mode is on, the values in testModeTemperature and testModeHumidity are written to tempIndoor and humIndoor by VenOS.
0x0311 | testModeTemperature | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value
0x0312 | testModeHumidity | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value
0x0313 | Zone2testModeTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value; to be written by VenOS to the 'Zone2tempIndoor' variable when in test mode.
0x0314 | Zone2testModeHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value; to be written by VenOS to the 'Zone2humIndoor' variable when in test mode.
0x0315 | Zone3testModeTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value
0x0316 | Zone3testModeHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value
0x0317 | Zone4testModeTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value
0x0318 | Zone4testModeHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value
0x0319 | Zone5testModeTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value
0x031A | Zone5testModeHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value
0x031B | Zone6testModeTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor temperature in 0.1deg C; 255: Sensor error value
0x031C | Zone6testModeHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Test indoor humidity; 255: Sensor error value
// Control of temp/hum data sources
0x0320 | tempHumControlSource | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat and/or remote sensors); 1: use P1P2 indoor unit sensor value stored in"P1P2IndoorSuctionAirThermistor" to write to "tempIndoor" and write "0xFF" to humIndoor; Overridden if "indoorRemoteSensorAveragingMethod" !="0" (is non zero); Only available for P1P2 systems;
0x0321 | indoorControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control when "indoorRemoteSensorAveragingMethod" is set to "1" or "2". Implemented in VenOS, may be added to UI in v3.4 release.
0x0322 | indoorRemoteSensorAveragingMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to tempIndoor and humIndoor by VenOS during normal operation.
0x0323 | homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x0324 | homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x0325 | homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x0326 | awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when away turns ON, except for when this variable is a '9' in which case nothing is copied;
0x0327 | awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when away turns ON;
0x0328 | awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when away turns ON, except for when this variable is a '9' in which case nothing is copied;
// RF temp/hum sensor #1
0x0330 | RFtempHumSensor1MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0331 | RFtempHumSensor1Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0332 | RFtempHumSensor1Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0333 | RFtempHumSensor1Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0334 | RFtempHumSensor1FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0335 | RFtempHumSensor1Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0336 | RFtempHumSensor1Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0337 | RFtempHumSensor1Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0338 | RFtempHumSensor1TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0339 | RFtempHumSensor1Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x033A | RFtempHumSensor1HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x033B | RFtempHumSensor1Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x033C | RFtempHumSensor1Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x033D | RFtempHumSensor1LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Time stamp of last sensor communication.
// RF temp/hum sensor #2
0x0340 | RFtempHumSensor2MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0341 | RFtempHumSensor2Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0342 | RFtempHumSensor2Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0343 | RFtempHumSensor2Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0344 | RFtempHumSensor2FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0345 | RFtempHumSensor2Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0346 | RFtempHumSensor2Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0347 | RFtempHumSensor2Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0348 | RFtempHumSensor2TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0349 | RFtempHumSensor2Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x034A | RFtempHumSensor2HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x034B | RFtempHumSensor2Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x034C | RFtempHumSensor2Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x034D | RFtempHumSensor2LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #3
0x0350 | RFtempHumSensor3MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0351 | RFtempHumSensor3Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0352 | RFtempHumSensor3Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0353 | RFtempHumSensor3Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0354 | RFtempHumSensor3FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0355 | RFtempHumSensor3Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0356 | RFtempHumSensor3Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0357 | RFtempHumSensor3Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0358 | RFtempHumSensor3TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0359 | RFtempHumSensor3Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x035A | RFtempHumSensor3HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x035B | RFtempHumSensor3Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x035C | RFtempHumSensor3Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x035D | RFtempHumSensor3LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #4
0x0360 | RFtempHumSensor4MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0361 | RFtempHumSensor4Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0362 | RFtempHumSensor4Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0363 | RFtempHumSensor4Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online.
0x0364 | RFtempHumSensor4FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0365 | RFtempHumSensor4Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0366 | RFtempHumSensor4Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0367 | RFtempHumSensor4Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0368 | RFtempHumSensor4TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0369 | RFtempHumSensor4Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x036A | RFtempHumSensor4HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x036B | RFtempHumSensor4Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x036C | RFtempHumSensor4Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x036D | RFtempHumSensor4LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #5
0x0370 | RFtempHumSensor5MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0371 | RFtempHumSensor5Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0372 | RFtempHumSensor5Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0373 | RFtempHumSensor5Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0374 | RFtempHumSensor5FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0375 | RFtempHumSensor5Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0376 | RFtempHumSensor5Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0377 | RFtempHumSensor5Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0378 | RFtempHumSensor5TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0379 | RFtempHumSensor5Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x037A | RFtempHumSensor5HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x037B | RFtempHumSensor5Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x037C | RFtempHumSensor5Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x037D | RFtempHumSensor5LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #6
0x0380 | RFtempHumSensor6MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0381 | RFtempHumSensor6Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0382 | RFtempHumSensor6Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0383 | RFtempHumSensor6Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0384 | RFtempHumSensor6FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0385 | RFtempHumSensor6Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0386 | RFtempHumSensor6Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0387 | RFtempHumSensor6Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0388 | RFtempHumSensor6TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0389 | RFtempHumSensor6Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x038A | RFtempHumSensor6HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x038B | RFtempHumSensor6Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x038C | RFtempHumSensor6Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x038D | RFtempHumSensor6LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #7
0x0390 | RFtempHumSensor7MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x0391 | RFtempHumSensor7Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0392 | RFtempHumSensor7Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0393 | RFtempHumSensor7Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x0394 | RFtempHumSensor7FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x0395 | RFtempHumSensor7Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0396 | RFtempHumSensor7Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x0397 | RFtempHumSensor7Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x0398 | RFtempHumSensor7TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x0399 | RFtempHumSensor7Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x039A | RFtempHumSensor7HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x039B | RFtempHumSensor7Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x039C | RFtempHumSensor7Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x039D | RFtempHumSensor7LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// RF temp/hum sensor #8
0x03A0 | RFtempHumSensor8MAC | CHAR | 0 | 17 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | WiFi MAC address; populated by VenOS
0x03A1 | RFtempHumSensor8Name | CHAR | 0 | 32 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor name entered in UI and written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x03A2 | RFtempHumSensor8Type | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: indoor; 1: outdoor; If outdoor cannot be used for "tempIndoor" control. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x03A3 | RFtempHumSensor8Online | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: FALSE; 1: TRUE; Used to report if sensor is online. Offline reported only after sensor has been ofline for at least 5 minutes continuously.
0x03A4 | RFtempHumSensor8FwVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | RHT temp/hum sensor FW version (not currently displayed in UI as of v3.6 release)
0x03A5 | RFtempHumSensor8Battery | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x03A6 | RFtempHumSensor8Signal | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0% to 100%, 0xFF means no data
0x03A7 | RFtempHumSensor8Temp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor temperature in 0.1deg C; 255: Sensor error value; value is after calibration applied;
0x03A8 | RFtempHumSensor8TempCal | FLOAT | -10 | 10 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the temperature measured by the sensor in 0.5deg C, as set in the installer sensor temperature calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x03A9 | RFtempHumSensor8Hum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is after calibration applied;
0x03AA | RFtempHumSensor8HumCal | INT8 | -30 | 30 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Offset to the humidity value measured by the sensor, as entered by the installer in the sensor humidity calibration screen. Written to the sensor through VenOS, and reported back to the datamap by VenOS.
0x03AB | RFtempHumSensor8Style | UINT8 | 0 | 2 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: wall-mount; 1: flush-mount; 2: Wireless (Zone) Thermostat; Wall-mount RHT sensors leave this as the default of 0 for its initial release, flush mount sensors will write a 1 to this variable, Wireless thermostats a 2.
0x03AC | RFtempHumSensor8Zone | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: no zone assignment; 1-6: Zones 1 to 6, respectively. Unassinged sensor will be treated as if assigned to zone 1 by VenOS.
0x03AD | RFtempHumSensor8LastActiveTime | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Time stamp of last sensor communication.
// Thermostat Errors (Last 20)
400 | sysFault1Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
401 | sysFault1Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
402 | sysFault2Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
403 | sysFault2Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
404 | sysFault3Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
405 | sysFault3Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
406 | sysFault4Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
407 | sysFault4Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
408 | sysFault5Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
409 | sysFault5Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
40A | sysFault6Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
40B | sysFault6Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
40C | sysFault7Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
40D | sysFault7Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
40E | sysFault8Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
40F | sysFault8Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
410 | sysFault9Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
411 | sysFault9Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
412 | sysFault10Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
413 | sysFault10Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
414 | sysFault11Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
415 | sysFault11Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
416 | sysFault12Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
417 | sysFault12Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
418 | sysFault13Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
419 | sysFault13Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
41A | sysFault14Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
41B | sysFault14Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
41C | sysFault15Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
41D | sysFault15Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
41E | sysFault16Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
41F | sysFault16Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
420 | sysFault17Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
421 | sysFault17Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
422 | sysFault18Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
423 | sysFault18Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
424 | sysFault19Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
425 | sysFault19Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
426 | sysFault20Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Date of the fault in Unix time.
427 | sysFault20Code | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Hex error code of the thermostat fault.
// RF temp/hum sensor #1, Wireless Tstat additions
0x0500 | RFtempHumSensor1equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x0501 | RFtempHumSensor1tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0502 | RFtempHumSensor1humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0503 | RFtempHumSensor1mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0504 | RFtempHumSensor1cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0505 | RFtempHumSensor1hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0506 | RFtempHumSensor1cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0507 | RFtempHumSensor1hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0508 | RFtempHumSensor1cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0509 | RFtempHumSensor1hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050A | RFtempHumSensor1tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050B | RFtempHumSensor1tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050C | RFtempHumSensor1tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050D | RFtempHumSensor1geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050E | RFtempHumSensor1schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x050F | RFtempHumSensor1schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0510 | RFtempHumSensor1fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0511 | RFtempHumSensor1fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0512 | RFtempHumSensor1ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x0513 | RFtempHumSensor1ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0514 | RFtempHumSensor1ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0515 | RFtempHumSensor1rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x0516 | RFtempHumSensor1rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #2, Wireless Tstat additions
0x0520 | RFtempHumSensor2equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x0521 | RFtempHumSensor2tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0522 | RFtempHumSensor2humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0523 | RFtempHumSensor2mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0524 | RFtempHumSensor2cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0525 | RFtempHumSensor2hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0526 | RFtempHumSensor2cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0527 | RFtempHumSensor2hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0528 | RFtempHumSensor2cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0529 | RFtempHumSensor2hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052A | RFtempHumSensor2tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052B | RFtempHumSensor2tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052C | RFtempHumSensor2tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052D | RFtempHumSensor2geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052E | RFtempHumSensor2schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x052F | RFtempHumSensor2schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0530 | RFtempHumSensor2fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0531 | RFtempHumSensor2fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0532 | RFtempHumSensor2ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x0533 | RFtempHumSensor2ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0534 | RFtempHumSensor2ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0535 | RFtempHumSensor2rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x0536 | RFtempHumSensor2rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #3, Wireless Tstat additions
0x0540 | RFtempHumSensor3equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x0541 | RFtempHumSensor3tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0542 | RFtempHumSensor3humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0543 | RFtempHumSensor3mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0544 | RFtempHumSensor3cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0545 | RFtempHumSensor3hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0546 | RFtempHumSensor3cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0547 | RFtempHumSensor3hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0548 | RFtempHumSensor3cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0549 | RFtempHumSensor3hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054A | RFtempHumSensor3tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054B | RFtempHumSensor3tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054C | RFtempHumSensor3tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054D | RFtempHumSensor3geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054E | RFtempHumSensor3schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x054F | RFtempHumSensor3schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0550 | RFtempHumSensor3fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0551 | RFtempHumSensor3fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0552 | RFtempHumSensor3ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x0553 | RFtempHumSensor3ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0554 | RFtempHumSensor3ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0555 | RFtempHumSensor3rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x0556 | RFtempHumSensor3rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #4, Wireless Tstat additions
0x0560 | RFtempHumSensor4equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x0561 | RFtempHumSensor4tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0562 | RFtempHumSensor4humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0563 | RFtempHumSensor4mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0564 | RFtempHumSensor4cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0565 | RFtempHumSensor4hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0566 | RFtempHumSensor4cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0567 | RFtempHumSensor4hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0568 | RFtempHumSensor4cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0569 | RFtempHumSensor4hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056A | RFtempHumSensor4tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056B | RFtempHumSensor4tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056C | RFtempHumSensor4tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056D | RFtempHumSensor4geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056E | RFtempHumSensor4schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x056F | RFtempHumSensor4schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0570 | RFtempHumSensor4fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0571 | RFtempHumSensor4fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0572 | RFtempHumSensor4ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x0573 | RFtempHumSensor4ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0574 | RFtempHumSensor4ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0575 | RFtempHumSensor4rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x0576 | RFtempHumSensor4rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #5, Wireless Tstat additions
0x0580 | RFtempHumSensor5equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x0581 | RFtempHumSensor5tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0582 | RFtempHumSensor5humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x0583 | RFtempHumSensor5mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0584 | RFtempHumSensor5cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0585 | RFtempHumSensor5hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0586 | RFtempHumSensor5cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0587 | RFtempHumSensor5hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0588 | RFtempHumSensor5cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0589 | RFtempHumSensor5hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058A | RFtempHumSensor5tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058B | RFtempHumSensor5tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058C | RFtempHumSensor5tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058D | RFtempHumSensor5geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058E | RFtempHumSensor5schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x058F | RFtempHumSensor5schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0590 | RFtempHumSensor5fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0591 | RFtempHumSensor5fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x0592 | RFtempHumSensor5ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x0593 | RFtempHumSensor5ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0594 | RFtempHumSensor5ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x0595 | RFtempHumSensor5rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x0596 | RFtempHumSensor5rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #6, Wireless Tstat additions
0x05A0 | RFtempHumSensor6equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x05A1 | RFtempHumSensor6tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05A2 | RFtempHumSensor6humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05A3 | RFtempHumSensor6mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x05A4 | RFtempHumSensor6cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05A5 | RFtempHumSensor6hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05A6 | RFtempHumSensor6cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05A7 | RFtempHumSensor6hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05A8 | RFtempHumSensor6cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05A9 | RFtempHumSensor6hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AA | RFtempHumSensor6tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AB | RFtempHumSensor6tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AC | RFtempHumSensor6tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AD | RFtempHumSensor6geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AE | RFtempHumSensor6schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05AF | RFtempHumSensor6schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05B0 | RFtempHumSensor6fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05B1 | RFtempHumSensor6fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05B2 | RFtempHumSensor6ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x05B3 | RFtempHumSensor6ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05B4 | RFtempHumSensor6ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05B5 | RFtempHumSensor6rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x05B6 | RFtempHumSensor6rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #7, Wireless Tstat additions
0x05C0 | RFtempHumSensor7equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x05C1 | RFtempHumSensor7tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05C2 | RFtempHumSensor7humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05C3 | RFtempHumSensor7mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x05C4 | RFtempHumSensor7cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05C5 | RFtempHumSensor7hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05C6 | RFtempHumSensor7cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05C7 | RFtempHumSensor7hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05C8 | RFtempHumSensor7cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05C9 | RFtempHumSensor7hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CA | RFtempHumSensor7tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CB | RFtempHumSensor7tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CC | RFtempHumSensor7tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CD | RFtempHumSensor7geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CE | RFtempHumSensor7schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05CF | RFtempHumSensor7schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05D0 | RFtempHumSensor7fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05D1 | RFtempHumSensor7fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05D2 | RFtempHumSensor7ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x05D3 | RFtempHumSensor7ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05D4 | RFtempHumSensor7ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05D5 | RFtempHumSensor7rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x05D6 | RFtempHumSensor7rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// RF temp/hum sensor #8, Wireless Tstat additions
0x05E0 | RFtempHumSensor8equipmentStatus | UINT8 | 1 | 9 | 5 | TRUE | READ | READWRITE | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen. Copied from the zone status of the assigned zone.
0x05E1 | RFtempHumSensor8tempIndoor | FLOAT | -40 | 60, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in 0.1deg C resolution; Copied from the zone indoor temperature (which is an average from all sensors in the zone) and displayed on the main screen of Wireless Zone Thermostats. The measured temp of the Wireless Tstat is reported in 'RFtempHumSensor1Temp', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05E2 | RFtempHumSensor8humIndoor | UINT8 | 0 | 100, 255 | 255 | TRUE | READ | READ | READ | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor humidity in 1% resolution; Copied from the zone indoor humidity (which is an average from all sensors in the zone) and possibly displayed in the Wireless Zone Thermostats screen. The measured hum of the Wireless Tstat is reported in 'RFtempHumSensor1Hum', and if this is the only sensor in this zone the reported values is copied back to this variable and sent back to the wireless thermostat for display.
0x05E3 | RFtempHumSensor8mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x05E4 | RFtempHumSensor8cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05E5 | RFtempHumSensor8hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05E6 | RFtempHumSensor8cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05E7 | RFtempHumSensor8hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05E8 | RFtempHumSensor8cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05E9 | RFtempHumSensor8hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05EA | RFtempHumSensor8tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05EB | RFtempHumSensor8tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05EC | RFtempHumSensor8tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05ED | RFtempHumSensor8geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05EE | RFtempHumSensor8schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05EF | RFtempHumSensor8schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05F0 | RFtempHumSensor8fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05F1 | RFtempHumSensor8fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Copied from the value for the zone.
0x05F2 | RFtempHumSensor8ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided to make a local setting only) 0: don't show clock; 1: display clock (Used for Wireless (zone) Tstat clock display)
0x05F3 | RFtempHumSensor8ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05F4 | RFtempHumSensor8ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Used to report critical faults generated within the Wireless (zone) thermostat.
0x05F5 | RFtempHumSensor8rawTemp | FLOAT | -90 | 60, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Raw sensor temperature in 0.1deg C; 255: Sensor error value; value is before TCE or calibration offsets applied;
0x05F6 | RFtempHumSensor8rawHum | UINT8 | 0 | 100, 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Sensor relative humidity in %; 255: Sensor error; value is before TCE or calibration offsets applied;
// SubGHz (VenNet) controller tracking variables
0x0600 | rfCoprocRestartCount | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | CC1350 restart count (UINT32)
0x0601 | rfCoprocUptime | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | CC1350 uptime (UINT32)
0x0602 | rfCoprocHostTxPackets | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | tx packets between host and CC1350 (UINT32)
0x0603 | rfCoprocHostRxPackets | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | rx packets between host and CC1350 (UINT32)
0x0604 | rfCoprocHostErrors | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | errors between host and CC1350 (UINT32)
0x0605 | rfCoprocHostTimeouts | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | timeouts between host and CC1350 (UINT32)
0x0606 | rfCoprocFwVersion | CHAR | 0 | 16 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | CC1350 firmware version string (char string like XXX.YYY.ZZZ, max 16 symbols should be fine)
0x0607 | rfCoprocActiveChannelNum | UINT8 | 0 | 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | optional: active channel number (uint8_t)
0x0608 | rfCoprocNetworkID | UINT8 | 0 | 255 | 255 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | optional: network ID (uint8_t)
//Zone Interface #1 (Wired Zone thermostat) System Status and Control
0x0800 | ZoneInt1equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from Zone[x]equipmentStatus variables instead) Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x0801 | ZoneInt1cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x0802 | ZoneInt1hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x0803 | ZoneInt1tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x0804 | ZoneInt1humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x0805 | ZoneInt1mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0806 | ZoneInt1control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x0807 | ZoneInt1deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
0x0808 | ZoneInt1deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | User entered custom thermostat name when deviceName is 0;
0x0809 | ZoneInt1schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x080A | ZoneInt1schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x080B | ZoneInt1schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x080C | ZoneInt1ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Used to report critical faults generated within the thermostat.
0x080D | ZoneInt1statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | DKN number written to thermostat by VenOS, starting in v3.3 release?
0x080E | ZoneInt1WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from "Zone[x]WiredSensorCalcTemp" variables instead); Zone board temperature sensor value in C after calibration from "Zone[x]WiredSensorCalcTemp" variable.
0x080F | ZoneInt1AssignedZone | UINT8 | 2 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0xFF: no zone assignment; 2-6: Zones 2 to 6, respectively. Unassinged zone interfaces are ignored.
//Zone Interface #1 (Wired Zone thermostat) Temperature, Humidity and Geofencing Settings
0x0820 | ZoneInt1cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0821 | ZoneInt1hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0822 | ZoneInt1cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0823 | ZoneInt1hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0824 | ZoneInt1cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x0825 | ZoneInt1hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x0826 | ZoneInt1tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0827 | ZoneInt1tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0828 | ZoneInt1tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x0829 | ZoneInt1humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x082A | ZoneInt1dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x082B | ZoneInt1overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x082C | ZoneInt1geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Zone Interface #1 (Wired Zone thermostat) Equipment Fan Settings
0x0840 | ZoneInt1fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x0841 | ZoneInt1fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x0842 | ZoneInt1fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x0843 | ZoneInt1fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x0844 | ZoneInt1fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x0845 | ZoneInt1fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x0846 | ZoneInt1oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
//Zone Interface #2 (Wired Zone thermostat) System Status and Control
0x0850 | ZoneInt2equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from Zone[x]equipmentStatus variables instead) Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x0851 | ZoneInt2cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x0852 | ZoneInt2hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x0853 | ZoneInt2tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x0854 | ZoneInt2humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x0855 | ZoneInt2mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0856 | ZoneInt2control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x0857 | ZoneInt2deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
0x0858 | ZoneInt2deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | User entered custom thermostat name when deviceName is 0;
0x0859 | ZoneInt2schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x085A | ZoneInt2schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x085B | ZoneInt2schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x085C | ZoneInt2ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Used to report critical faults generated within the thermostat.
0x085D | ZoneInt2statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | DKN number written to thermostat by VenOS, starting in v3.3 release?
0x085E | ZoneInt2WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from "Zone[x]WiredSensorCalcTemp" variables instead); Zone board temperature sensor value in C after calibration from "Zone[x]WiredSensorCalcTemp" variable.
0x085F | ZoneInt2AssignedZone | UINT8 | 2 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0xFF: no zone assignment; 2-6: Zones 2 to 6, respectively. Unassinged zone interfaces are ignored.
//Zone Interface #2 (Wired Zone thermostat) Temperature, Humidity and Geofencing Settings
0x0870 | ZoneInt2cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0871 | ZoneInt2hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0872 | ZoneInt2cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0873 | ZoneInt2hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0874 | ZoneInt2cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x0875 | ZoneInt2hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x0876 | ZoneInt2tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0877 | ZoneInt2tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0878 | ZoneInt2tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x0879 | ZoneInt2humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x087A | ZoneInt2dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x087B | ZoneInt2overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x087C | ZoneInt2geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Zone Interface #2 (Wired Zone thermostat) Equipment Fan Settings
0x0890 | ZoneInt2fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x0891 | ZoneInt2fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x0892 | ZoneInt2fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x0893 | ZoneInt2fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x0894 | ZoneInt2fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x0895 | ZoneInt2fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x0896 | ZoneInt2oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
//Zone Interface #3 (Wired Zone thermostat) System Status and Control
0x08A0 | ZoneInt3equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from Zone[x]equipmentStatus variables instead) Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x08A1 | ZoneInt3cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x08A2 | ZoneInt3hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x08A3 | ZoneInt3tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x08A4 | ZoneInt3humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x08A5 | ZoneInt3mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x08A6 | ZoneInt3control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x08A7 | ZoneInt3deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
0x08A8 | ZoneInt3deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | User entered custom thermostat name when deviceName is 0;
0x08A9 | ZoneInt3schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x08AA | ZoneInt3schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x08AB | ZoneInt3schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x08AC | ZoneInt3ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Used to report critical faults generated within the thermostat.
0x08AD | ZoneInt3statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | DKN number written to thermostat by VenOS, starting in v3.3 release?
0x08AE | ZoneInt3WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from "Zone[x]WiredSensorCalcTemp" variables instead); Zone board temperature sensor value in C after calibration from "Zone[x]WiredSensorCalcTemp" variable.
0x08AF | ZoneInt3AssignedZone | UINT8 | 2 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0xFF: no zone assignment; 2-6: Zones 2 to 6, respectively. Unassinged zone interfaces are ignored.
//Zone Interface #3 (Wired Zone thermostat) Temperature, Humidity and Geofencing Settings
0x08C0 | ZoneInt3cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x08C1 | ZoneInt3hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x08C2 | ZoneInt3cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x08C3 | ZoneInt3hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x08C4 | ZoneInt3cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x08C5 | ZoneInt3hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x08C6 | ZoneInt3tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x08C7 | ZoneInt3tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x08C8 | ZoneInt3tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x08C9 | ZoneInt3humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x08CA | ZoneInt3dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x08CB | ZoneInt3overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x08CC | ZoneInt3geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Zone Interface #3 (Wired Zone thermostat) Equipment Fan Settings
0x08E0 | ZoneInt3fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x08E1 | ZoneInt3fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x08E2 | ZoneInt3fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x08E3 | ZoneInt3fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x08E4 | ZoneInt3fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x08E5 | ZoneInt3fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x08E6 | ZoneInt3oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
//Zone Interface #4 (Wired Zone thermostat) System Status and Control
0x0900 | ZoneInt4equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from Zone[x]equipmentStatus variables instead) Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x0901 | ZoneInt4cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x0902 | ZoneInt4hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x0903 | ZoneInt4tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x0904 | ZoneInt4humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x0905 | ZoneInt4mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0906 | ZoneInt4control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x0907 | ZoneInt4deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
0x0908 | ZoneInt4deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | User entered custom thermostat name when deviceName is 0;
0x0909 | ZoneInt4schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x090A | ZoneInt4schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x090B | ZoneInt4schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x090C | ZoneInt4ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Used to report critical faults generated within the thermostat.
0x090D | ZoneInt4statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | DKN number written to thermostat by VenOS, starting in v3.3 release?
0x090E | ZoneInt4WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from "Zone[x]WiredSensorCalcTemp" variables instead); Zone board temperature sensor value in C after calibration from "Zone[x]WiredSensorCalcTemp" variable.
0x090F | ZoneInt4AssignedZone | UINT8 | 2 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0xFF: no zone assignment; 2-6: Zones 2 to 6, respectively. Unassinged zone interfaces are ignored.
//Zone Interface #4 (Wired Zone thermostat) Temperature, Humidity and Geofencing Settings
0x0920 | ZoneInt4cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0921 | ZoneInt4hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0922 | ZoneInt4cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0923 | ZoneInt4hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0924 | ZoneInt4cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x0925 | ZoneInt4hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x0926 | ZoneInt4tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0927 | ZoneInt4tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0928 | ZoneInt4tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x0929 | ZoneInt4humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x092A | ZoneInt4dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x092B | ZoneInt4overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x092C | ZoneInt4geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Zone Interface #4 (Wired Zone thermostat) Equipment Fan Settings
0x0940 | ZoneInt4fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x0941 | ZoneInt4fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x0942 | ZoneInt4fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x0943 | ZoneInt4fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x0944 | ZoneInt4fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x0945 | ZoneInt4fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x0946 | ZoneInt4oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
//Zone Interface #5 (Wired Zone thermostat) System Status and Control
0x0950 | ZoneInt5equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from Zone[x]equipmentStatus variables instead) Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x0951 | ZoneInt5cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x0952 | ZoneInt5hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x0953 | ZoneInt5tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x0954 | ZoneInt5humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x0955 | ZoneInt5mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x0956 | ZoneInt5control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x0957 | ZoneInt5deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "deviceNameCustom" is used as the device name.
0x0958 | ZoneInt5deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | User entered custom thermostat name when deviceName is 0;
0x0959 | ZoneInt5schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x095A | ZoneInt5schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x095B | ZoneInt5schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x095C | ZoneInt5ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Used to report critical faults generated within the thermostat.
0x095D | ZoneInt5statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | DKN number written to thermostat by VenOS, starting in v3.3 release?
0x095E | ZoneInt5WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED (decided Z.I.s will pull directly from "Zone[x]WiredSensorCalcTemp" variables instead); Zone board temperature sensor value in C after calibration from "Zone[x]WiredSensorCalcTemp" variable.
0x095F | ZoneInt5AssignedZone | UINT8 | 2 | 6, 0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | 0xFF: no zone assignment; 2-6: Zones 2 to 6, respectively. Unassinged zone interfaces are ignored.
//Zone Interface #5 (Wired Zone thermostat) Temperature, Humidity and Geofencing Settings
0x0970 | ZoneInt5cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0971 | ZoneInt5hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x0972 | ZoneInt5cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0973 | ZoneInt5hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x0974 | ZoneInt5cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x0975 | ZoneInt5hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x0976 | ZoneInt5tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0977 | ZoneInt5tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x0978 | ZoneInt5tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x0979 | ZoneInt5humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x097A | ZoneInt5dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x097B | ZoneInt5overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x097C | ZoneInt5geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
//Zone Interface #5 (Wired Zone thermostat) Equipment Fan Settings
0x0990 | ZoneInt5fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x0991 | ZoneInt5fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x0992 | ZoneInt5fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x0993 | ZoneInt5fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x0994 | ZoneInt5fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x0995 | ZoneInt5fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x0996 | ZoneInt5oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
//General Zoning and Zone Board variables.
0x1000 | zoneBoardModel | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Model number reported by zone board.
0x1001 | zoneBoardMACaddress | CHAR | 0 | 17 | NULL | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address reported by zone board.
0x1002 | zoneBoardSerialNum | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Serial Number reported by zone board.
0x1003 | zoneBoardFwVersion | CHAR | 0 | 8 | NULL | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Firmware version reported by zone board.
0x1004 | zoneBoardSupplyAirTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Supply air temp reported by zone board.
0x1005 | zoneBoardReturnAirTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Return air temp reported by zone board.
0x1006 | zoneBoardDiffPressure | INT16 | -1000 | 10000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Differential pressure sensor reading reported by zone board.
0x1007 | zoneBoardTestModeStatus | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Off; 1: On;
0x1008 | zoneBoardSafetyModeStatus | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Off; 1: On;
0x1009 | zoneBoardLeakModeStatus | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no leak; 1: leak detected;
0x100A | zoneBoardBLEstatus | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TBD
0x100B | zoneBoardCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Critical Fault reported by the zone board or zoning control algorithm.
0x100C | zoneBoardMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Minor fault reported by the zone board or zoning control algorithm.
0x100D | zoneBoardDamperDetectStatus | UINT8 | 0 | 3 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: not run yet; 1: start auto detect; 2: running; 3: complete; cannot start until dampers are motionless.
0x100E | zoneDamperScalingFactor | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone damper position scaling factor in percent, used for opening largest demand zone damper to 100% to minimize static pressure.
0x100F | allZoneAutoWeightStatus | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: not run yet; 1 run/complete; 2: running;
0x1010 | reliefZonesActive | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no relief zones active; >0: relief zones activated; used by zoning control algorithm to indicate when the relief zone strategy is active and which zones are being used for relief. Bit 0 indicates relief zones are active, bits 1-6 which of zones 1-6, respectively, are relief zones.
0x1011 | ctAHBlowerMotorMaxCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Max CFM capability reported by the air handler, used for zone weights when requesting indoor unit heat or airflow.
0x1012 | ctIFCBlowerMotorMaxCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Max CFM capability reported by the furnace, used for zone weights when requesting indoor unit heat or airflow.
0x1020 | zoneBoardAux1ZStatus | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Off; 1: On;
0x1021 | zoneBoardAux2ZStatus | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Off; 1: On;
0x1022 | zoneBoardBulkDataPack | CHAR | 0 | 512 | NULL | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0x1023 | zoneBoardBulkDataPackNum | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | packet number current during transaction
0x1024 | zoneBoardFwUpdateStatus | UINT8 | 0 | 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: idle; 1: firmware update in progress; 2: update found, but not started; 3: firmware update completed.
0x1025 | zoneBoardDamperTravelTime | UINT8 | 0 | 60 | 35 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Travel time in seconds (from 5 to 60 seconds in 5s steps);
0x1026 | singleZoneOperation | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Off; 1: On; Used by control algorithm to indicate when single-zone operation is active, because of loss of communication with with the zone board, with all additional zone thermostats and sensors. or other similar conditions.
0x1027 | zoneBoardUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
0x1028 | zoneBoardBulkDataTotalPackets | UINT16 | 0 | 0xFFFF | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Total number of packets in a zone board firmware update; reported by VenOS to allows PIC24 CT code to manage the update over ClimateTalk.
0x1029 | ctUnitControlType | UINT8 | 1 | 2 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 1: Primary zone thermostat; 2: Wired Zone thermostat (aka Zone Interface)
0x102A | ctUnitNodeAddress | UINT8 | 0 | 255 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Address on ClimateTalk bus, per zoning control logic
0x102B | ZoneIntConnected | UINT8 | 0 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Each bit Indicates zone interface connected status over CT bus. bit0- ZoneInt1 , bit1- ZoneInt2 ,bit2- ZoneInt3 , bit3- ZoneInt4 ,bit4- ZoneInt5 . bit( 1- connected 0: disconnected). Will be used for debug purpose for now.
0x102C | CurrentViewedZone | UINT8 | 0 | 6 | 1 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: none/error state (light pipe off); Values 1-6 indicate zones 1-6, respectively; The UI writes to this to indicate which zone is currently being viewed. VenOS uses this zone's "Zone[x]equipmentStatus" variable to activate the light pipe on the primary zone thermostat. For zone 1, the "equipmentStatus" continues to be used.
0x102D | zoningEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Tied to checkbox in UI so installer can disable zoning and operate system as a single zone. UI should prompt to enable at end of comissioning process if zone board found but this variable disabled.
0x1030 | ZoningTestMode | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; Used by UI to start and stop the zoning test algorithm, using the "Zone#Test OpenPercent" variables as inputs.
0x1031 | Zone1TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1032 | Zone2TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1033 | Zone3TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1034 | Zone4TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1035 | Zone5TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1036 | Zone6TestOpenPercent | UINT8 | 0 | 100 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0 to 100%; open percent of damper during zoning test mode.
0x1037 | ZoneTotalCurrentXair | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Current Excess Air in the System. Need to divided by 100 before using.
0x1038 | ZoneTotalCallingAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Sum of all calling Zone CFM
0x1039 | ZoneCalculatedAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Current airflow in system, calculated based on the combination of the actual indoor airflow and requested demand .
0x103A | ODUtoIDUcurrentAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Indoor actual airflow from Indoor status message captured from status message requested by Outdoor
0x103B | ODUtoIDURequestedFanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Outdoor requested fan demand in %
//Zone 1 Additional System Status and Control
0x1060 | Zone1DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1061 | Zone1Enable | UINT8 | 0 | 1, 0xFF | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1062 | Zone1AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Copied from "Zone1MeasuredCFM" when running the the auto weight algorithm and preserved until next auto-weight algorithm run.
0x1063 | Zone1Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x1064 | Zone1Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x1065 | Zone1DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper position for the zone based on demand from the zoning control algorithm, before scaling and other adjustments.
0x1066 | Zone1ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x1067 | Zone1AutoWeightStatus | UINT8 | 0 | 2 | 0 | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: not run; 1 run/complete; 2: running;
0x1068 | Zone1Name | CHAR | 0 | 32 | Zone1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone name copied from thermostat or RHT sensor name, or manually entered.
0x1069 | Zone1MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x106A | Zone1SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. In the v3.7.5 release the user sets the weight in percent and this value is calculated based on the IDU max CFM. In the future, we want the UI to change this value directly, and then used this to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x106B | Zone1LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x106C | Zone1AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x1070 | Zone1WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature from the zone board temp sensor.
0x1071 | Zone1WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration to the zone board temp sensor.
0x1072 | Zone1WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value after calibration.
0x1073 | Zone1WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 2 System Status and Control
0x1080 | Zone2equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x1081 | Zone2cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x1082 | Zone2hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x1083 | Zone2tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x1084 | Zone2humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x1085 | Zone2mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x1086 | Zone2control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x1087 | Zone2DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1088 | Zone2Enable | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1089 | Zone2AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Max CFM for this zone as determined by the auto weight algorithm. Preserved until next auto-weight algorithm run.
0x108A | Zone2Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x108B | Zone2Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x108C | Zone2DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper open % for the zone based on demand from the zoning control algorithm; this is the value before scaling and other adjustments.
0x108D | Zone2ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x108E | Zone2Name | CHAR | 0 | 32 | Zone2 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | NOT USED after v3.7.2 release; Manually entered zone name; may be inherited from a thermostat or sensor assigned to that zone; Will use "Zone[x]deviceName" and "Zone[x]deviceNameCustom" variables instead.
0x108F | Zone2ControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control when "Zone2SensorAvgMethod" is set to "1" or "2". Used by VenOS to determine zone temperature.
0x1090 | Zone2SensorAvgMethod | UINT8 | 0 | 4 | 4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to the zone's tempIndoor and humIndoor by VenOS during normal operation.
0x1091 | Zone2mergedWithZone1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: operating as independent zone; 1: merged with Zone 1; Set by control algorithm when a zone is enabled but cannot operate independently due to no active sensors or thermostats in that zone.
0x1092 | Zone2MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x1093 | Zone2SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. A user may change this value directly, and it is then used to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x1094 | Zone2LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x1095 | Zone2deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "Zone[x]deviceNameCustom" is used as the device name.
0x1096 | Zone2deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when Zone[x]deviceName is 0;
0x1097 | Zone2AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x10A0 | Zone2WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature in C from the zone board temp sensor for this zone.
0x10A1 | Zone2WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration offset in C to the zone board temp sensor.
0x10A2 | Zone2WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value in C after calibration.
0x10A3 | Zone2WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 2 Temperature, Humidity and Geofencing Settings
0x10B0 | Zone2cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x10B1 | Zone2hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x10B2 | Zone2cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x10B3 | Zone2hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x10B4 | Zone2cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x10B5 | Zone2hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x10B6 | Zone2tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x10B7 | Zone2tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x10B8 | Zone2tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x10B9 | Zone2humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x10BA | Zone2dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x10BB | Zone2humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
0x10BC | Zone2overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x10BD | Zone2geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
0x10C0 | Zone2homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x10C1 | Zone2homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x10C2 | Zone2homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x10C3 | Zone2awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
0x10C4 | Zone2awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when this schedule event becomes active;
0x10C5 | Zone2awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
//Zone 2 Equipment Fan Settings
0x10D0 | Zone2fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x10D1 | Zone2fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x10D2 | Zone2fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x10D3 | Zone2fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x10D4 | Zone2fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x10D5 | Zone2fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x10D6 | Zone2oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x10D7 | Zone2oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
//Zone 3 System Status and Control
0x1100 | Zone3equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x1101 | Zone3cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x1102 | Zone3hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x1103 | Zone3tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x1104 | Zone3humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x1105 | Zone3mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x1106 | Zone3control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x1107 | Zone3DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1108 | Zone3Enable | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1109 | Zone3AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Max CFM for this zone as determined by the auto weight algorithm. Preserved until next auto-weight algorithm run.
0x110A | Zone3Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x110B | Zone3Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x110C | Zone3DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper open % for the zone based on demand from the zoning control algorithm; this is the value before scaling and other adjustments.
0x110D | Zone3ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x110E | Zone3Name | CHAR | 0 | 32 | Zone3 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED after v3.7.2 release; Manually entered zone name; may be inherited from a thermostat or sensor assigned to that zone; Will use "Zone[x]deviceName" and "Zone[x]deviceNameCustom" variables instead.
0x110F | Zone3ControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control when "Zone2SensorAvgMethod" is set to "1" or "2". Used by VenOS to determine zone temperature.
0x1110 | Zone3SensorAvgMethod | UINT8 | 0 | 4 | 4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to the zone's tempIndoor and humIndoor by VenOS during normal operation.
0x1111 | Zone3mergedWithZone1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: operating as independent zone; 1: merged with Zone 1; Set by control algorithm when a zone is enabled but cannot operate independently due to no active sensors or thermostats in that zone.
0x1112 | Zone3MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x1113 | Zone3SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. A user may change this value directly, and it is then used to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x1114 | Zone3LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x1115 | Zone3deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "Zone[x]deviceNameCustom" is used as the device name.
0x1116 | Zone3deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when Zone[x]deviceName is 0;
0x1117 | Zone3AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x1120 | Zone3WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature in C from the zone board temp sensor for this zone.
0x1121 | Zone3WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration offset in C to the zone board temp sensor.
0x1122 | Zone3WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value in C after calibration.
0x1123 | Zone3WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 3 Temperature, Humidity and Geofencing Settings
0x1130 | Zone3cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x1131 | Zone3hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x1132 | Zone3cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x1133 | Zone3hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x1134 | Zone3cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x1135 | Zone3hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x1136 | Zone3tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x1137 | Zone3tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x1138 | Zone3tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x1139 | Zone3humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x113A | Zone3dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x113B | Zone3humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
0x113C | Zone3overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x113D | Zone3geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
0x1140 | Zone3homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1141 | Zone3homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1142 | Zone3homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1143 | Zone3awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
0x1144 | Zone3awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when this schedule event becomes active;
0x1145 | Zone3awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
//Zone 3 Equipment Fan Settings
0x1150 | Zone3fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x1151 | Zone3fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x1152 | Zone3fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x1153 | Zone3fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x1154 | Zone3fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x1155 | Zone3fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x1156 | Zone3oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x1157 | Zone3oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
//Zone 4 System Status and Control
0x1180 | Zone4equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x1181 | Zone4cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x1182 | Zone4hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x1183 | Zone4tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x1184 | Zone4humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x1185 | Zone4mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x1186 | Zone4control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x1187 | Zone4DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1188 | Zone4Enable | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1189 | Zone4AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Max CFM for this zone as determined by the auto weight algorithm. Preserved until next auto-weight algorithm run.
0x118A | Zone4Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x118B | Zone4Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x118C | Zone4DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper open % for the zone based on demand from the zoning control algorithm; this is the value before scaling and other adjustments.
0x118D | Zone4ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x118E | Zone4Name | CHAR | 0 | 32 | Zone4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED after v3.7.2 release; Manually entered zone name; may be inherited from a thermostat or sensor assigned to that zone; Will use "Zone[x]deviceName" and "Zone[x]deviceNameCustom" variables instead.
0x118F | Zone4ControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control when "Zone2SensorAvgMethod" is set to "1" or "2". Used by VenOS to determine zone temperature.
0x1190 | Zone4SensorAvgMethod | UINT8 | 0 | 4 | 4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to the zone's tempIndoor and humIndoor by VenOS during normal operation.
0x1191 | Zone4mergedWithZone1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: operating as independent zone; 1: merged with Zone 1; Set by control algorithm when a zone is enabled but cannot operate independently due to no active sensors or thermostats in that zone.
0x1192 | Zone4MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x1193 | Zone4SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. A user may change this value directly, and it is then used to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x1194 | Zone4LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x1195 | Zone4deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "Zone[x]deviceNameCustom" is used as the device name.
0x1196 | Zone4deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when Zone[x]deviceName is 0;
0x1197 | Zone4AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x11A0 | Zone4WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature in C from the zone board temp sensor for this zone.
0x11A1 | Zone4WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration offset in C to the zone board temp sensor.
0x11A2 | Zone4WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value in C after calibration.
0x11A3 | Zone4WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 4 Temperature, Humidity and Geofencing Settings
0x11B0 | Zone4cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x11B1 | Zone4hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x11B2 | Zone4cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x11B3 | Zone4hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x11B4 | Zone4cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x11B5 | Zone4hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x11B6 | Zone4tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x11B7 | Zone4tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x11B8 | Zone4tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x11B9 | Zone4humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x11BA | Zone4dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x11BB | Zone4humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
0x11BC | Zone4overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x11BD | Zone4geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
0x11C0 | Zone4homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x11C1 | Zone4homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x11C2 | Zone4homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x11C3 | Zone4awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
0x11C4 | Zone4awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when this schedule event becomes active;
0x11C5 | Zone4awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
//Zone 4 Equipment Fan Settings
0x11D0 | Zone4fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x11D1 | Zone4fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x11D2 | Zone4fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x11D3 | Zone4fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x11D4 | Zone4fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x11D5 | Zone4fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x11D6 | Zone4oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x11D7 | Zone4oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
//Zone 5 System Status and Control
0x1200 | Zone5equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x1201 | Zone5cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x1202 | Zone5hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x1203 | Zone5tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x1204 | Zone5humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x1205 | Zone5mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x1206 | Zone5control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x1207 | Zone5DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1208 | Zone5Enable | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1209 | Zone5AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Max CFM for this zone as determined by the auto weight algorithm. Preserved until next auto-weight algorithm run.
0x120A | Zone5Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x120B | Zone5Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x120C | Zone5DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper open % for the zone based on demand from the zoning control algorithm; this is the value before scaling and other adjustments.
0x120D | Zone5ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x120E | Zone5Name | CHAR | 0 | 32 | Zone5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED after v3.7.2 release; Manually entered zone name; may be inherited from a thermostat or sensor assigned to that zone; Will use "Zone[x]deviceName" and "Zone[x]deviceNameCustom" variables instead.
0x120F | Zone5ControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control when "Zone2SensorAvgMethod" is set to "1" or "2". Used by VenOS to determine zone temperature.
0x1210 | Zone5SensorAvgMethod | UINT8 | 0 | 4 | 4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to the zone's tempIndoor and humIndoor by VenOS during normal operation.
0x1211 | Zone5mergedWithZone1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: operating as independent zone; 1: merged with Zone 1; Set by control algorithm when a zone is enabled but cannot operate independently due to no active sensors or thermostats in that zone.
0x1212 | Zone5MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x1213 | Zone5SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. A user may change this value directly, and it is then used to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x1214 | Zone5LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x1215 | Zone5deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "Zone[x]deviceNameCustom" is used as the device name.
0x1216 | Zone5deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when Zone[x]deviceName is 0;
0x1217 | Zone5AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x1220 | Zone5WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature in C from the zone board temp sensor for this zone.
0x1221 | Zone5WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration offset in C to the zone board temp sensor.
0x1222 | Zone5WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value in C after calibration.
0x1223 | Zone5WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 5 Temperature, Humidity and Geofencing Settings
0x1230 | Zone5cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x1231 | Zone5hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x1232 | Zone5cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x1233 | Zone5hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x1234 | Zone5cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x1235 | Zone5hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x1236 | Zone5tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x1237 | Zone5tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x1238 | Zone5tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x1239 | Zone5humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x123A | Zone5dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x123B | Zone5humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
0x123C | Zone5overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x123D | Zone5geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
0x1240 | Zone5homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1241 | Zone5homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1242 | Zone5homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x1243 | Zone5awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
0x1244 | Zone5awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when this schedule event becomes active;
0x1245 | Zone5awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
//Zone 5 Equipment Fan Settings
0x1250 | Zone5fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x1251 | Zone5fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x1252 | Zone5fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x1253 | Zone5fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x1254 | Zone5fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x1255 | Zone5fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x1256 | Zone5oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x1257 | Zone5oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
//Zone 6 System Status and Control
0x1280 | Zone6equipmentStatus | UINT8 | 1 | 9 | 5 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Equipment status; 1: cool; 2: overcool for dehum; 3: heat; 4: fan; 5: idle; 6: waiting to cool; 7: waiting to heat; 8: aux humidifier (NOT USED); 9: aux dehumidifier (NOT USED); Used by UI software to color the system mode icon, to turn on the light pipe or LED to indicate heating or cooling, and to display status message on the main screen.
0x1281 | Zone6cspActive | FLOAT | 10 | 32.2 | 23 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current cooling setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment, and copied by VenOS from cspHome, cspAway, or cspSched depending on the currently setpoints being used for control.
0x1282 | Zone6hspActive | FLOAT | 10 | 32.2 | 21 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current heating setpoint in C with 0.1 deg C resolution; used by protocol software to control the HVAC equipment and copied by VenOS from hspHome, hspAway, or hspSched depending on the currently setpoints being used for control.
0x1283 | Zone6tempIndoor | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor temperature in C with 0.1deg C resolution; 255: Sensor error. Displayed on the main screen and as the indoor temperature on the air quality screen, and used by protocol software to control the equipment. If wireless RHT sensors or the IDU sensor (for VRV) is in use, this value is an average of some combination of the thermostat and/or the other sensors' temperature readings, as selected in the settings for those sensors.
0x1284 | Zone6humIndoor | UINT8 | 0 | 100, 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current indoor relative humidity in %; 255: Sensor error; Used for the indoor humidity displayed on the air quality screen and by the protocol software to determine if humidification or dehumidification is needed. If wireless RHT sensors, this value is an average of some combination of the thermostat and/or the other sensors' humidity readings, as selected in the settings for those sensors.
0x1285 | Zone6mode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode (fan and dry mode are only supported by P1P2 and S21 equipment); As of the v2.7 software release fan mode is supported as a hidden feature in the UI and by the P1P2/S21 code since the v2.5 release.
0x1286 | Zone6control | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: home, 1: away, 2: schedule; Only written by VenOS to indicate which setpoints are currently being used;
0x1287 | Zone6DamperAutoDetect | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: no damper; 1: damper detected; 0xFF never written before. Written by the damper auto-detect algorithm in the zone board.
0x1288 | Zone6Enable | UINT8 | 0 | 1, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; 0xFF never written before. If 0xFF or 0, is automatically overwritten by value in 'ZonexDamperAutoDetect' when damper auto-detect is run. If '1', the thermostat generates an error code if auto-detect for this zone returns a '0', and if in the commissioning screens the UI also generates a confirmation message asking if they want to disable this zone before overwriting to a '0'.
0x1289 | Zone6AutoWeightCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Max CFM for this zone as determined by the auto weight algorithm. Preserved until next auto-weight algorithm run.
0x128A | Zone6Weight | UINT8 | 0 | 100 | 50 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone weight in % used along with the "Zone[x]SelectedCFM" by the control algorithm ; These two should always be written together, with "Zone[x]Weight" = "Zone2SelectedCFM" / (IDU max CFM), whenever auto-weight is run or whenever the user manually selects a zone weight or Max CFM in the UI. These can be restored manually by the user from last auto weight value.
0x128B | Zone6Voting | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: non-voting; 1: voting; All zones are voting by default. Installer may make some zones non-voting.
0x128C | Zone6DamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Current requested damper open % for the zone based on demand from the zoning control algorithm; this is the value before scaling and other adjustments.
0x128D | Zone6ScaledDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Damper position after scaling for 100% damper open for the zone with the largest demand, to minimize the static pressure introduced by the dampers.
0x128E | Zone6Name | CHAR | 0 | 32 | Zone6 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED after v3.7.2 release; Manually entered zone name; may be inherited from a thermostat or sensor assigned to that zone; Will use "Zone[x]deviceName" and "Zone[x]deviceNameCustom" variables instead.
0x128F | Zone6ControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control when "Zone2SensorAvgMethod" is set to "1" or "2". Used by VenOS to determine zone temperature.
0x1290 | Zone6SensorAvgMethod | UINT8 | 0 | 4 | 4 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; determines source(s) of the temp and hum written to the zone's tempIndoor and humIndoor by VenOS during normal operation.
0x1291 | Zone6mergedWithZone1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: operating as independent zone; 1: merged with Zone 1; Set by control algorithm when a zone is enabled but cannot operate independently due to no active sensors or thermostats in that zone.
0x1292 | Zone6MeasuredCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's auto-measured max CFM value. It is copied to the "Zone1AutoWeightCFM" and to "Zone1SelectedCFM" when auto-weight is run, but otherwise gathered periodically to measure the max CFM in each zone and generate a minor error if significantly higher (in blocked duct conditions) or lower (leaking duct conditions) than the "Zone1AutoWeightCFM" value.
0x1293 | Zone6SelectedCFM | UINT16 | 0 | 0xFFFF | 0xFFFF | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | This is the zone's max CFM used by the control algorithm. It is copied from "Zone1AutoWeightCFM" when auto-weight is run and is always the same as the "Zone1AutoWeightCFM" value if the user has not manually changed the zone weight. A user may change this value directly, and it is then used to calculate the zone weights for indoor operation and outdoor operation, which are displayed for reference.
0x1294 | Zone6LastMeasuredCFMtime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | Unix timestamp of last time valid "Zone[x]MeasuredCFM" value was recorded.
0x1295 | Zone6deviceName | UINT8 | 0 | 7 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Thermostat name; 0: other, 1: main room, 2: upstairs, 3: downstairs, 4: basement, 5: hallway, 6: bedroom, 7: kitchen; If "0: other" is selected, then the text stored in "Zone[x]deviceNameCustom" is used as the device name.
0x1296 | Zone6deviceNameCustom | CHAR | 0 | 32 | Other | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User entered custom thermostat name when Zone[x]deviceName is 0;
0x1297 | Zone6AdjDamperPosition | UINT8 | 0 | 100, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Final damper position sent to zone board after adjusting for excess air needs of entire system.
0x12A0 | Zone6WiredSensorTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Raw temperature in C from the zone board temp sensor for this zone.
0x12A1 | Zone6WiredSensorTempCal | FLOAT | -10 | 10 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Calibration offset in C to the zone board temp sensor.
0x12A2 | Zone6WiredSensorCalcTemp | FLOAT | -40 | 60, 255 | 255 | FALSE | READ | READ | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Zone board temperature sensor value in C after calibration.
0x12A3 | Zone6WiredSensorEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; Enabled by installer in UI if wired sensor installed.
//Zone 6 Temperature, Humidity and Geofencing Settings
0x12B0 | Zone6cspHome | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Manual" or home operating mode in 0.1deg C; written from UI and copied to "cspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x12B1 | Zone6hspHome | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Manual" operating mode in 0.1deg C; written from UI and copied to "hspActive" by VenOS whenever the thermostat changes from Away or Schedule to Home mode.
0x12B2 | Zone6cspAway | FLOAT | 10 | 32.2 | 28 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling threshold for the "Away" operating mode in 0.1deg C. Copied to "cspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x12B3 | Zone6hspAway | FLOAT | 10 | 32.2 | 16 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Away" operating mode in 0.1deg C. Copied to "hspActive" by VenOS whenever "geofencingAway" is TRUE or "control" is "1: Away".
0x12B4 | Zone6cspSched | FLOAT | 10 | 32.2 | 23 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for the "Schedule" operating mode in 0.1deg C. Copied from the csp of the applicable schedule event by VenOS, and copied to cspActive by VenOS when schedule is active.
0x12B5 | Zone6hspSched | FLOAT | 10 | 32.2 | 21 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating threshold for the "Schedule" operating mode in 0.1deg C. Copied from the hsp of the applicable schedule event by VenOS, and copied to "hspActive" by VenOS when schedule is active.
0x12B6 | Zone6tempSPMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Minimum temperature setpoint allowed in homeowner UI. Starts with minimum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x12B7 | Zone6tempSPMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Maximum temperature setpoint allowed in homeowner UI. Starts with maximum determined from equipment protocol type, and is further restricted in installer menus and saved in this variable. The starting value for the P1P2 and S21 protocols was hard coded into the v2.7.10 UI, but started using the "EquipProtocolMaxCoolSetpoint" and "EquipProtocolMaxHeatSetpoint" variables in the v3.2.1 release for the Lite and the v3.2.19 release for the rest of the thermostats.
0x12B8 | Zone6tempDeltaMin | FLOAT | 1 | 5 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP and CSP minimum delta in 0.5deg C. Enforced by the UI software when being set but not enforced when written to datamap by equipment, cloud, or OpenAPI unless the UI's there enforce it.
0x12B9 | Zone6humSP | UINT8 | 0 | 75 | 40 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Humidification setpoint selected in the homeowner UI. The UI enforces 5% steps and a minimum of 25% in the v2.7 release, and enforces a 75% minus humDeltaMin of 10%, or 65% maximum.
0x12BA | Zone6dehumSP | UINT8 | 25 | 75 | 55 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Dehumidification setpoint selected in the homeonwer UI. The UI enfoces a 5% step size and a mimum of 25% plus the humDeltaMin of 10%, or 35%, in the v2.7 release.
0x12BB | Zone6humDeltaMin | UINT8 | 5 | 10 | 10 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT AVAILABE AS SETTING, plan to leave at 10. Is minimum difference between humSP and dehumSP.
0x12BC | Zone6overcoolAmount | FLOAT | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Amount of overcool allows to dehumidify in 0.5C° steps. Used by protocol software to keep cooling the equipment cooling past the setpoint.
0x12BD | Zone6geofencingAway | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE (some devices are home); 1: TRUE (all devices are away). Set to "1" by Skyport when all geofencing devices are away (if geofencing enabled in homeowner app) or to "1" by UI if Away turned on manually. Set to "0" by Skyport if a geofencing device comes home, or if Away turned off manually.
0x12C0 | Zone6homeSystemMode | UINT8 | 0 | 6 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "mode" selection is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x12C1 | Zone6homeControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control; The "indoorControlSensorMAC" adress is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x12C2 | Zone6homeSensorAvgMethod | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; The value of "indoorRemoteSensorAveragingMethod" is saved here when Away or Schedule are turned ON, and restored from here when they are turned OFF.
0x12C3 | Zone6awaySystemMode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: no change; The "awaySystemMode" is copied to the "mode" variable when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
0x12C4 | Zone6awayControlSensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | MAC address of RF sensor used for control. If "awaySensorAvgMethod" is a '1' or '2', "awayControlSensorMAC" is copied to "indoorControlSensorMAC" when this schedule event becomes active;
0x12C5 | Zone6awaySensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: no change; "awaySensorAvgMethod" is copied to "indoorRemoteSensorAveragingMethod" when this schedule event becomes active, except for when this variable is a '9' in which case nothing is copied;
//Zone 6 Equipment Fan Settings
0x12D0 | Zone6fanCirculate | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Run the fan on a schedule; 0: off, 1: always on, 2: on a schedule; In v2.7 only used by CT protocol code to activate fan, but is trumped by heat or cool fan demand.
0x12D1 | Zone6fanCirculateActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: on; Activated according to fan schedule by VenOS, and can be turned off by UI to pause the fan schedule. Only used if "fanCirculate" set to "2: on a schedule".
0x12D2 | Zone6fanCirculateDuration | UINT8 | 0 | 4 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time (in ms) to run the fan per hour when circulating on a schedule 0: continuous, 1: 300000 (5 minutes), 2: 900000 (15 minutes), 3: 1.8e+6 (30 minutes), 4: 2.7e+6 (45 minutes)
0x12D3 | Zone6fanCirculateSpeed | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed at which fan should run when always on or when circulating on a schedule. Trumped by heat or cool fan demand.
0x12D4 | Zone6fanCirculateStart | UINT8 | 0 | 95 | 48 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time of scheduled air circulation in 15 minute increments; default is noon local time.
0x12D5 | Zone6fanCirculateStop | UINT8 | 0 | 95 | 72 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | End time of scheduled air circulation in 15 minute increments, default is 6pm local time.
0x12D6 | Zone6oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x12D7 | Zone6oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
//Zone 2 Schedule
0x1400 | Zone2schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x1401 | Zone2schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x1402 | Zone2schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
0x1403 | Zone2schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x1404 | Zone2schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1405 | Zone2schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1406 | Zone2schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1407 | Zone2schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1408 | Zone2schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1409 | Zone2schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x140A | Zone2schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x140B | Zone2schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x140C | Zone2schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x140D | Zone2schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x140E | Zone2schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x140F | Zone2schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1410 | Zone2schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1411 | Zone2schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1412 | Zone2schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1413 | Zone2schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1414 | Zone2schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1415 | Zone2schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1416 | Zone2schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1417 | Zone2schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1418 | Zone2schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1419 | Zone2schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x141A | Zone2schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x141B | Zone2schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x141C | Zone2schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x141D | Zone2schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x141E | Zone2schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x141F | Zone2schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1420 | Zone2schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1421 | Zone2schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1422 | Zone2schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1423 | Zone2schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1424 | Zone2schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1425 | Zone2schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1426 | Zone2schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1427 | Zone2schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1428 | Zone2schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1429 | Zone2schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x142A | Zone2schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x142B | Zone2schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x142C | Zone2schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x142D | Zone2schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x142E | Zone2schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x142F | Zone2schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1430 | Zone2schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1431 | Zone2schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1432 | Zone2schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1433 | Zone2schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1434 | Zone2schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1435 | Zone2schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1436 | Zone2schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1437 | Zone2schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1438 | Zone2schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1439 | Zone2schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x143A | Zone2schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x143B | Zone2schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x143C | Zone2schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x143D | Zone2schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x143E | Zone2schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x143F | Zone2schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1440 | Zone2schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1441 | Zone2schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1442 | Zone2schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1443 | Zone2schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1444 | Zone2schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1445 | Zone2schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1446 | Zone2schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1447 | Zone2schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1448 | Zone2schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1449 | Zone2schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x144A | Zone2schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x144B | Zone2schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x144C | Zone2schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x144D | Zone2schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x144E | Zone2schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x144F | Zone2schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1450 | Zone2schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1451 | Zone2schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1452 | Zone2schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1453 | Zone2schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1454 | Zone2schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1455 | Zone2schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1456 | Zone2schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1457 | Zone2schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1458 | Zone2schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1459 | Zone2schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x145A | Zone2schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x145B | Zone2schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x145C | Zone2schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x145D | Zone2schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x145E | Zone2schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x145F | Zone2schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1460 | Zone2schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1461 | Zone2schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1462 | Zone2schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1463 | Zone2schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1464 | Zone2schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1465 | Zone2schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1466 | Zone2schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1467 | Zone2schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1468 | Zone2schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1469 | Zone2schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x146A | Zone2schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x146B | Zone2schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x146C | Zone2schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x146D | Zone2schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x146E | Zone2schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x146F | Zone2schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1470 | Zone2schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1471 | Zone2schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1472 | Zone2schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1473 | Zone2schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1474 | Zone2schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1475 | Zone2schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1476 | Zone2schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1477 | Zone2schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1478 | Zone2schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1479 | Zone2schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x147A | Zone2schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x147B | Zone2schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x147C | Zone2schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x147D | Zone2schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x147E | Zone2schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x147F | Zone2schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1480 | Zone2schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1481 | Zone2schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1482 | Zone2schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1483 | Zone2schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1484 | Zone2schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1485 | Zone2schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1486 | Zone2schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1487 | Zone2schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1488 | Zone2schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1489 | Zone2schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x148A | Zone2schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x148B | Zone2schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x148C | Zone2schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x148D | Zone2schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x148E | Zone2schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x148F | Zone2schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1490 | Zone2schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1491 | Zone2schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1492 | Zone2schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1493 | Zone2schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1494 | Zone2schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1495 | Zone2schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1496 | Zone2schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1497 | Zone2schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1498 | Zone2schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1499 | Zone2schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x149A | Zone2schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x149B | Zone2schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x149C | Zone2schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x149D | Zone2schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x149E | Zone2schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x149F | Zone2schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14A0 | Zone2schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14A1 | Zone2schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x14A2 | Zone2schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14A3 | Zone2schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14A4 | Zone2schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14A5 | Zone2schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14A6 | Zone2schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14A7 | Zone2schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x14A8 | Zone2schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14A9 | Zone2schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14AA | Zone2schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14AB | Zone2schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14AC | Zone2schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14AD | Zone2schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14AE | Zone2schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14AF | Zone2schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14B0 | Zone2schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14B1 | Zone2schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14B2 | Zone2schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14B3 | Zone2schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14B4 | Zone2schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14B5 | Zone2schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14B6 | Zone2schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14B7 | Zone2schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14B8 | Zone2schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14B9 | Zone2schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x14BA | Zone2schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14BB | Zone2schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14BC | Zone2schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14BD | Zone2schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14BE | Zone2schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14BF | Zone2schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x14C0 | Zone2schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14C1 | Zone2schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14C2 | Zone2schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14C3 | Zone2schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14C4 | Zone2schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14C5 | Zone2schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x14C6 | Zone2schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14C7 | Zone2schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14C8 | Zone2schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14C9 | Zone2schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14CA | Zone2schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14CB | Zone2schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x14CC | Zone2schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14CD | Zone2schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14CE | Zone2schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14CF | Zone2schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14D0 | Zone2schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14D1 | Zone2schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14D2 | Zone2schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14D3 | Zone2schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14D4 | Zone2schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14D5 | Zone2schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14D6 | Zone2schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14D7 | Zone2schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14D8 | Zone2schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14D9 | Zone2schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14DA | Zone2schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14DB | Zone2schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14DC | Zone2schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14DD | Zone2schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x14DE | Zone2schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14DF | Zone2schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14E0 | Zone2schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14E1 | Zone2schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14E2 | Zone2schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14E3 | Zone2schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x14E4 | Zone2schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14E5 | Zone2schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14E6 | Zone2schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14E7 | Zone2schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14E8 | Zone2schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14E9 | Zone2schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x14EA | Zone2schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14EB | Zone2schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14EC | Zone2schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14ED | Zone2schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14EE | Zone2schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x14EF | Zone2schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x14F0 | Zone2schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14F1 | Zone2schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14F2 | Zone2schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14F3 | Zone2schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14F4 | Zone2schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14F5 | Zone2schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14F6 | Zone2schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14F7 | Zone2schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14F8 | Zone2schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14F9 | Zone2schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x14FA | Zone2schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x14FB | Zone2schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x14FC | Zone2schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x14FD | Zone2schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x14FE | Zone2schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x14FF | Zone2schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//Zone 3 Schedule
0x1500 | Zone3schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x1501 | Zone3schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x1502 | Zone3schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
0x1503 | Zone3schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x1504 | Zone3schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1505 | Zone3schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1506 | Zone3schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1507 | Zone3schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1508 | Zone3schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1509 | Zone3schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x150A | Zone3schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x150B | Zone3schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x150C | Zone3schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x150D | Zone3schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x150E | Zone3schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x150F | Zone3schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1510 | Zone3schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1511 | Zone3schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1512 | Zone3schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1513 | Zone3schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1514 | Zone3schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1515 | Zone3schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1516 | Zone3schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1517 | Zone3schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1518 | Zone3schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1519 | Zone3schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x151A | Zone3schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x151B | Zone3schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x151C | Zone3schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x151D | Zone3schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x151E | Zone3schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x151F | Zone3schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1520 | Zone3schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1521 | Zone3schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1522 | Zone3schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1523 | Zone3schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1524 | Zone3schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1525 | Zone3schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1526 | Zone3schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1527 | Zone3schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1528 | Zone3schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1529 | Zone3schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x152A | Zone3schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x152B | Zone3schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x152C | Zone3schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x152D | Zone3schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x152E | Zone3schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x152F | Zone3schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1530 | Zone3schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1531 | Zone3schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1532 | Zone3schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1533 | Zone3schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1534 | Zone3schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1535 | Zone3schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1536 | Zone3schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1537 | Zone3schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1538 | Zone3schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1539 | Zone3schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x153A | Zone3schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x153B | Zone3schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x153C | Zone3schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x153D | Zone3schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x153E | Zone3schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x153F | Zone3schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1540 | Zone3schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1541 | Zone3schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1542 | Zone3schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1543 | Zone3schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1544 | Zone3schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1545 | Zone3schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1546 | Zone3schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1547 | Zone3schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1548 | Zone3schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1549 | Zone3schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x154A | Zone3schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x154B | Zone3schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x154C | Zone3schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x154D | Zone3schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x154E | Zone3schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x154F | Zone3schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1550 | Zone3schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1551 | Zone3schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1552 | Zone3schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1553 | Zone3schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1554 | Zone3schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1555 | Zone3schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1556 | Zone3schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1557 | Zone3schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1558 | Zone3schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1559 | Zone3schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x155A | Zone3schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x155B | Zone3schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x155C | Zone3schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x155D | Zone3schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x155E | Zone3schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x155F | Zone3schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1560 | Zone3schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1561 | Zone3schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1562 | Zone3schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1563 | Zone3schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1564 | Zone3schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1565 | Zone3schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1566 | Zone3schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1567 | Zone3schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1568 | Zone3schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1569 | Zone3schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x156A | Zone3schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x156B | Zone3schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x156C | Zone3schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x156D | Zone3schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x156E | Zone3schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x156F | Zone3schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1570 | Zone3schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1571 | Zone3schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1572 | Zone3schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1573 | Zone3schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1574 | Zone3schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1575 | Zone3schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1576 | Zone3schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1577 | Zone3schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1578 | Zone3schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1579 | Zone3schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x157A | Zone3schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x157B | Zone3schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x157C | Zone3schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x157D | Zone3schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x157E | Zone3schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x157F | Zone3schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1580 | Zone3schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1581 | Zone3schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1582 | Zone3schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1583 | Zone3schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1584 | Zone3schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1585 | Zone3schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1586 | Zone3schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1587 | Zone3schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1588 | Zone3schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1589 | Zone3schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x158A | Zone3schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x158B | Zone3schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x158C | Zone3schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x158D | Zone3schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x158E | Zone3schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x158F | Zone3schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1590 | Zone3schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1591 | Zone3schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1592 | Zone3schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1593 | Zone3schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1594 | Zone3schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1595 | Zone3schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1596 | Zone3schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1597 | Zone3schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1598 | Zone3schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1599 | Zone3schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x159A | Zone3schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x159B | Zone3schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x159C | Zone3schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x159D | Zone3schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x159E | Zone3schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x159F | Zone3schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15A0 | Zone3schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15A1 | Zone3schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x15A2 | Zone3schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15A3 | Zone3schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15A4 | Zone3schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15A5 | Zone3schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15A6 | Zone3schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15A7 | Zone3schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x15A8 | Zone3schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15A9 | Zone3schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15AA | Zone3schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15AB | Zone3schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15AC | Zone3schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15AD | Zone3schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15AE | Zone3schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15AF | Zone3schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15B0 | Zone3schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15B1 | Zone3schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15B2 | Zone3schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15B3 | Zone3schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15B4 | Zone3schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15B5 | Zone3schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15B6 | Zone3schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15B7 | Zone3schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15B8 | Zone3schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15B9 | Zone3schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x15BA | Zone3schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15BB | Zone3schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15BC | Zone3schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15BD | Zone3schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15BE | Zone3schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15BF | Zone3schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x15C0 | Zone3schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15C1 | Zone3schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15C2 | Zone3schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15C3 | Zone3schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15C4 | Zone3schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15C5 | Zone3schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x15C6 | Zone3schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15C7 | Zone3schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15C8 | Zone3schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15C9 | Zone3schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15CA | Zone3schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15CB | Zone3schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x15CC | Zone3schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15CD | Zone3schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15CE | Zone3schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15CF | Zone3schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15D0 | Zone3schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15D1 | Zone3schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15D2 | Zone3schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15D3 | Zone3schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15D4 | Zone3schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15D5 | Zone3schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15D6 | Zone3schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15D7 | Zone3schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15D8 | Zone3schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15D9 | Zone3schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15DA | Zone3schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15DB | Zone3schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15DC | Zone3schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15DD | Zone3schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x15DE | Zone3schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15DF | Zone3schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15E0 | Zone3schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15E1 | Zone3schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15E2 | Zone3schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15E3 | Zone3schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x15E4 | Zone3schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15E5 | Zone3schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15E6 | Zone3schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15E7 | Zone3schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15E8 | Zone3schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15E9 | Zone3schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x15EA | Zone3schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15EB | Zone3schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15EC | Zone3schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15ED | Zone3schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15EE | Zone3schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x15EF | Zone3schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x15F0 | Zone3schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15F1 | Zone3schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15F2 | Zone3schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15F3 | Zone3schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15F4 | Zone3schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15F5 | Zone3schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15F6 | Zone3schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15F7 | Zone3schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15F8 | Zone3schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15F9 | Zone3schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x15FA | Zone3schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x15FB | Zone3schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x15FC | Zone3schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x15FD | Zone3schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x15FE | Zone3schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x15FF | Zone3schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//Zone 4 Schedule
0x1600 | Zone4schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x1601 | Zone4schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x1602 | Zone4schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
0x1603 | Zone4schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x1604 | Zone4schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1605 | Zone4schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1606 | Zone4schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1607 | Zone4schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1608 | Zone4schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1609 | Zone4schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x160A | Zone4schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x160B | Zone4schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x160C | Zone4schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x160D | Zone4schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x160E | Zone4schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x160F | Zone4schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1610 | Zone4schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1611 | Zone4schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1612 | Zone4schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1613 | Zone4schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1614 | Zone4schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1615 | Zone4schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1616 | Zone4schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1617 | Zone4schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1618 | Zone4schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1619 | Zone4schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x161A | Zone4schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x161B | Zone4schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x161C | Zone4schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x161D | Zone4schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x161E | Zone4schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x161F | Zone4schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1620 | Zone4schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1621 | Zone4schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1622 | Zone4schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1623 | Zone4schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1624 | Zone4schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1625 | Zone4schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1626 | Zone4schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1627 | Zone4schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1628 | Zone4schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1629 | Zone4schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x162A | Zone4schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x162B | Zone4schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x162C | Zone4schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x162D | Zone4schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x162E | Zone4schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x162F | Zone4schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1630 | Zone4schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1631 | Zone4schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1632 | Zone4schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1633 | Zone4schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1634 | Zone4schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1635 | Zone4schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1636 | Zone4schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1637 | Zone4schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1638 | Zone4schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1639 | Zone4schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x163A | Zone4schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x163B | Zone4schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x163C | Zone4schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x163D | Zone4schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x163E | Zone4schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x163F | Zone4schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1640 | Zone4schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1641 | Zone4schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1642 | Zone4schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1643 | Zone4schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1644 | Zone4schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1645 | Zone4schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1646 | Zone4schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1647 | Zone4schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1648 | Zone4schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1649 | Zone4schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x164A | Zone4schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x164B | Zone4schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x164C | Zone4schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x164D | Zone4schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x164E | Zone4schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x164F | Zone4schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1650 | Zone4schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1651 | Zone4schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1652 | Zone4schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1653 | Zone4schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1654 | Zone4schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1655 | Zone4schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1656 | Zone4schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1657 | Zone4schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1658 | Zone4schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1659 | Zone4schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x165A | Zone4schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x165B | Zone4schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x165C | Zone4schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x165D | Zone4schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x165E | Zone4schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x165F | Zone4schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1660 | Zone4schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1661 | Zone4schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1662 | Zone4schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1663 | Zone4schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1664 | Zone4schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1665 | Zone4schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1666 | Zone4schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1667 | Zone4schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1668 | Zone4schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1669 | Zone4schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x166A | Zone4schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x166B | Zone4schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x166C | Zone4schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x166D | Zone4schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x166E | Zone4schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x166F | Zone4schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1670 | Zone4schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1671 | Zone4schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1672 | Zone4schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1673 | Zone4schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1674 | Zone4schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1675 | Zone4schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1676 | Zone4schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1677 | Zone4schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1678 | Zone4schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1679 | Zone4schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x167A | Zone4schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x167B | Zone4schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x167C | Zone4schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x167D | Zone4schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x167E | Zone4schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x167F | Zone4schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1680 | Zone4schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1681 | Zone4schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1682 | Zone4schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1683 | Zone4schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1684 | Zone4schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1685 | Zone4schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1686 | Zone4schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1687 | Zone4schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1688 | Zone4schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1689 | Zone4schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x168A | Zone4schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x168B | Zone4schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x168C | Zone4schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x168D | Zone4schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x168E | Zone4schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x168F | Zone4schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1690 | Zone4schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1691 | Zone4schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1692 | Zone4schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1693 | Zone4schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1694 | Zone4schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1695 | Zone4schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1696 | Zone4schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1697 | Zone4schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1698 | Zone4schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1699 | Zone4schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x169A | Zone4schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x169B | Zone4schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x169C | Zone4schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x169D | Zone4schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x169E | Zone4schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x169F | Zone4schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16A0 | Zone4schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16A1 | Zone4schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x16A2 | Zone4schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16A3 | Zone4schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16A4 | Zone4schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16A5 | Zone4schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16A6 | Zone4schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16A7 | Zone4schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x16A8 | Zone4schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16A9 | Zone4schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16AA | Zone4schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16AB | Zone4schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16AC | Zone4schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16AD | Zone4schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16AE | Zone4schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16AF | Zone4schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16B0 | Zone4schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16B1 | Zone4schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16B2 | Zone4schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16B3 | Zone4schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16B4 | Zone4schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16B5 | Zone4schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16B6 | Zone4schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16B7 | Zone4schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16B8 | Zone4schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16B9 | Zone4schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x16BA | Zone4schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16BB | Zone4schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16BC | Zone4schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16BD | Zone4schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16BE | Zone4schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16BF | Zone4schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x16C0 | Zone4schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16C1 | Zone4schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16C2 | Zone4schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16C3 | Zone4schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16C4 | Zone4schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16C5 | Zone4schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x16C6 | Zone4schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16C7 | Zone4schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16C8 | Zone4schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16C9 | Zone4schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16CA | Zone4schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16CB | Zone4schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x16CC | Zone4schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16CD | Zone4schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16CE | Zone4schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16CF | Zone4schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16D0 | Zone4schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16D1 | Zone4schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16D2 | Zone4schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16D3 | Zone4schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16D4 | Zone4schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16D5 | Zone4schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16D6 | Zone4schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16D7 | Zone4schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16D8 | Zone4schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16D9 | Zone4schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16DA | Zone4schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16DB | Zone4schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16DC | Zone4schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16DD | Zone4schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x16DE | Zone4schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16DF | Zone4schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16E0 | Zone4schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16E1 | Zone4schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16E2 | Zone4schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16E3 | Zone4schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x16E4 | Zone4schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16E5 | Zone4schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16E6 | Zone4schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16E7 | Zone4schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16E8 | Zone4schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16E9 | Zone4schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x16EA | Zone4schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16EB | Zone4schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16EC | Zone4schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16ED | Zone4schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16EE | Zone4schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x16EF | Zone4schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x16F0 | Zone4schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16F1 | Zone4schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16F2 | Zone4schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16F3 | Zone4schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16F4 | Zone4schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16F5 | Zone4schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16F6 | Zone4schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16F7 | Zone4schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16F8 | Zone4schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16F9 | Zone4schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x16FA | Zone4schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x16FB | Zone4schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x16FC | Zone4schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x16FD | Zone4schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x16FE | Zone4schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x16FF | Zone4schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//Zone 5 Schedule
0x1700 | Zone5schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x1701 | Zone5schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x1702 | Zone5schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
0x1703 | Zone5schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x1704 | Zone5schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1705 | Zone5schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1706 | Zone5schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1707 | Zone5schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1708 | Zone5schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1709 | Zone5schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x170A | Zone5schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x170B | Zone5schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x170C | Zone5schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x170D | Zone5schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x170E | Zone5schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x170F | Zone5schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1710 | Zone5schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1711 | Zone5schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1712 | Zone5schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1713 | Zone5schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1714 | Zone5schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1715 | Zone5schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1716 | Zone5schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1717 | Zone5schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1718 | Zone5schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1719 | Zone5schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x171A | Zone5schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x171B | Zone5schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x171C | Zone5schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x171D | Zone5schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x171E | Zone5schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x171F | Zone5schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1720 | Zone5schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1721 | Zone5schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1722 | Zone5schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1723 | Zone5schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1724 | Zone5schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1725 | Zone5schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1726 | Zone5schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1727 | Zone5schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1728 | Zone5schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1729 | Zone5schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x172A | Zone5schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x172B | Zone5schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x172C | Zone5schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x172D | Zone5schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x172E | Zone5schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x172F | Zone5schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1730 | Zone5schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1731 | Zone5schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1732 | Zone5schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1733 | Zone5schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1734 | Zone5schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1735 | Zone5schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1736 | Zone5schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1737 | Zone5schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1738 | Zone5schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1739 | Zone5schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x173A | Zone5schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x173B | Zone5schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x173C | Zone5schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x173D | Zone5schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x173E | Zone5schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x173F | Zone5schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1740 | Zone5schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1741 | Zone5schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1742 | Zone5schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1743 | Zone5schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1744 | Zone5schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1745 | Zone5schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1746 | Zone5schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1747 | Zone5schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1748 | Zone5schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1749 | Zone5schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x174A | Zone5schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x174B | Zone5schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x174C | Zone5schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x174D | Zone5schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x174E | Zone5schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x174F | Zone5schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1750 | Zone5schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1751 | Zone5schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1752 | Zone5schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1753 | Zone5schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1754 | Zone5schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1755 | Zone5schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1756 | Zone5schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1757 | Zone5schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1758 | Zone5schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1759 | Zone5schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x175A | Zone5schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x175B | Zone5schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x175C | Zone5schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x175D | Zone5schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x175E | Zone5schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x175F | Zone5schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1760 | Zone5schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1761 | Zone5schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1762 | Zone5schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1763 | Zone5schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1764 | Zone5schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1765 | Zone5schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1766 | Zone5schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1767 | Zone5schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1768 | Zone5schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1769 | Zone5schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x176A | Zone5schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x176B | Zone5schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x176C | Zone5schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x176D | Zone5schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x176E | Zone5schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x176F | Zone5schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1770 | Zone5schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1771 | Zone5schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1772 | Zone5schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1773 | Zone5schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1774 | Zone5schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1775 | Zone5schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1776 | Zone5schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1777 | Zone5schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1778 | Zone5schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1779 | Zone5schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x177A | Zone5schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x177B | Zone5schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x177C | Zone5schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x177D | Zone5schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x177E | Zone5schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x177F | Zone5schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1780 | Zone5schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1781 | Zone5schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1782 | Zone5schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1783 | Zone5schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1784 | Zone5schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1785 | Zone5schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1786 | Zone5schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1787 | Zone5schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1788 | Zone5schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1789 | Zone5schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x178A | Zone5schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x178B | Zone5schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x178C | Zone5schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x178D | Zone5schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x178E | Zone5schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x178F | Zone5schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1790 | Zone5schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1791 | Zone5schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1792 | Zone5schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1793 | Zone5schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1794 | Zone5schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1795 | Zone5schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1796 | Zone5schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1797 | Zone5schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1798 | Zone5schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1799 | Zone5schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x179A | Zone5schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x179B | Zone5schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x179C | Zone5schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x179D | Zone5schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x179E | Zone5schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x179F | Zone5schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17A0 | Zone5schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17A1 | Zone5schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x17A2 | Zone5schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17A3 | Zone5schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17A4 | Zone5schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17A5 | Zone5schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17A6 | Zone5schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17A7 | Zone5schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x17A8 | Zone5schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17A9 | Zone5schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17AA | Zone5schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17AB | Zone5schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17AC | Zone5schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17AD | Zone5schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17AE | Zone5schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17AF | Zone5schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17B0 | Zone5schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17B1 | Zone5schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17B2 | Zone5schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17B3 | Zone5schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17B4 | Zone5schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17B5 | Zone5schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17B6 | Zone5schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17B7 | Zone5schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17B8 | Zone5schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17B9 | Zone5schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x17BA | Zone5schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17BB | Zone5schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17BC | Zone5schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17BD | Zone5schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17BE | Zone5schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17BF | Zone5schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x17C0 | Zone5schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17C1 | Zone5schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17C2 | Zone5schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17C3 | Zone5schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17C4 | Zone5schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17C5 | Zone5schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x17C6 | Zone5schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17C7 | Zone5schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17C8 | Zone5schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17C9 | Zone5schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17CA | Zone5schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17CB | Zone5schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x17CC | Zone5schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17CD | Zone5schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17CE | Zone5schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17CF | Zone5schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17D0 | Zone5schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17D1 | Zone5schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17D2 | Zone5schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17D3 | Zone5schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17D4 | Zone5schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17D5 | Zone5schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17D6 | Zone5schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17D7 | Zone5schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17D8 | Zone5schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17D9 | Zone5schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17DA | Zone5schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17DB | Zone5schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17DC | Zone5schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17DD | Zone5schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x17DE | Zone5schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17DF | Zone5schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17E0 | Zone5schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17E1 | Zone5schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17E2 | Zone5schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17E3 | Zone5schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x17E4 | Zone5schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17E5 | Zone5schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17E6 | Zone5schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17E7 | Zone5schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17E8 | Zone5schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17E9 | Zone5schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x17EA | Zone5schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17EB | Zone5schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17EC | Zone5schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17ED | Zone5schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17EE | Zone5schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x17EF | Zone5schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x17F0 | Zone5schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17F1 | Zone5schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17F2 | Zone5schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17F3 | Zone5schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17F4 | Zone5schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17F5 | Zone5schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17F6 | Zone5schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17F7 | Zone5schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17F8 | Zone5schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17F9 | Zone5schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x17FA | Zone5schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x17FB | Zone5schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x17FC | Zone5schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x17FD | Zone5schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x17FE | Zone5schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x17FF | Zone5schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//Zone 6 Schedule
0x1800 | Zone6schedEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: disabled; 1: enabled; records when the schedule is enabled by the user; Stays enabled if schedule paused by Skyport changing "geofencingAway" to 1 or by a manual temperature adjustment; Disabled by UI if Away turned on manually or if scheduled turned off.
0x1801 | Zone6schedOverride | UINT8 | 0 | 2 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: off (schedule not overridden), 1: home (schedule paused by manual temperature adjustment), 2: away (NOT USED); If the schedule is enabled ("schedEnabled"=1), this variable tells if the schedule is currently active or if a manual adjustment has overridden the schedule temporarily.
0x1802 | Zone6schedOverrideDuration | UINT16 | 0 | 480 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Duration in minutes that manual schedule override should remain in effect; 0: until next event, >0: minutes.
0x1803 | Zone6schedResumeTime | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Time at which normal schedule operation should resume. Set by VenOS when the schedule is overriden, and used by VenOS return to the schedule setpoints.
0x1804 | Zone6schedMonPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1805 | Zone6schedMonPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1806 | Zone6schedMonPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1807 | Zone6schedMonPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1808 | Zone6schedMonPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1809 | Zone6schedMonPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x180A | Zone6schedMonPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x180B | Zone6schedMonPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x180C | Zone6schedMonPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x180D | Zone6schedMonPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x180E | Zone6schedMonPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x180F | Zone6schedMonPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1810 | Zone6schedMonPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1811 | Zone6schedMonPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1812 | Zone6schedMonPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1813 | Zone6schedMonPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1814 | Zone6schedMonPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1815 | Zone6schedMonPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1816 | Zone6schedMonPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1817 | Zone6schedMonPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1818 | Zone6schedMonPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1819 | Zone6schedMonPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x181A | Zone6schedMonPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x181B | Zone6schedMonPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x181C | Zone6schedMonPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x181D | Zone6schedMonPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x181E | Zone6schedMonPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x181F | Zone6schedMonPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1820 | Zone6schedMonPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1821 | Zone6schedMonPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1822 | Zone6schedMonPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1823 | Zone6schedMonPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1824 | Zone6schedMonPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1825 | Zone6schedMonPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1826 | Zone6schedMonPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1827 | Zone6schedMonPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1828 | Zone6schedTuePart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1829 | Zone6schedTuePart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x182A | Zone6schedTuePart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x182B | Zone6schedTuePart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x182C | Zone6schedTuePart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x182D | Zone6schedTuePart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x182E | Zone6schedTuePart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x182F | Zone6schedTuePart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1830 | Zone6schedTuePart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1831 | Zone6schedTuePart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1832 | Zone6schedTuePart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1833 | Zone6schedTuePart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1834 | Zone6schedTuePart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1835 | Zone6schedTuePart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x1836 | Zone6schedTuePart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1837 | Zone6schedTuePart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1838 | Zone6schedTuePart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1839 | Zone6schedTuePart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x183A | Zone6schedTuePart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x183B | Zone6schedTuePart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x183C | Zone6schedTuePart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x183D | Zone6schedTuePart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x183E | Zone6schedTuePart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x183F | Zone6schedTuePart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1840 | Zone6schedTuePart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1841 | Zone6schedTuePart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1842 | Zone6schedTuePart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1843 | Zone6schedTuePart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1844 | Zone6schedTuePart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1845 | Zone6schedTuePart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1846 | Zone6schedTuePart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1847 | Zone6schedTuePart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1848 | Zone6schedTuePart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1849 | Zone6schedTuePart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x184A | Zone6schedTuePart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x184B | Zone6schedTuePart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x184C | Zone6schedWedPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x184D | Zone6schedWedPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x184E | Zone6schedWedPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x184F | Zone6schedWedPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1850 | Zone6schedWedPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1851 | Zone6schedWedPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1852 | Zone6schedWedPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1853 | Zone6schedWedPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1854 | Zone6schedWedPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1855 | Zone6schedWedPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1856 | Zone6schedWedPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1857 | Zone6schedWedPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1858 | Zone6schedWedPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1859 | Zone6schedWedPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x185A | Zone6schedWedPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x185B | Zone6schedWedPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x185C | Zone6schedWedPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x185D | Zone6schedWedPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x185E | Zone6schedWedPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x185F | Zone6schedWedPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1860 | Zone6schedWedPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1861 | Zone6schedWedPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1862 | Zone6schedWedPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1863 | Zone6schedWedPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1864 | Zone6schedWedPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1865 | Zone6schedWedPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1866 | Zone6schedWedPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1867 | Zone6schedWedPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1868 | Zone6schedWedPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1869 | Zone6schedWedPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x186A | Zone6schedWedPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x186B | Zone6schedWedPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x186C | Zone6schedWedPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x186D | Zone6schedWedPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x186E | Zone6schedWedPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x186F | Zone6schedWedPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1870 | Zone6schedThuPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1871 | Zone6schedThuPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1872 | Zone6schedThuPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1873 | Zone6schedThuPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1874 | Zone6schedThuPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1875 | Zone6schedThuPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1876 | Zone6schedThuPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1877 | Zone6schedThuPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x1878 | Zone6schedThuPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1879 | Zone6schedThuPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x187A | Zone6schedThuPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x187B | Zone6schedThuPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x187C | Zone6schedThuPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x187D | Zone6schedThuPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x187E | Zone6schedThuPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x187F | Zone6schedThuPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1880 | Zone6schedThuPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1881 | Zone6schedThuPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1882 | Zone6schedThuPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1883 | Zone6schedThuPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x1884 | Zone6schedThuPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1885 | Zone6schedThuPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1886 | Zone6schedThuPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1887 | Zone6schedThuPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1888 | Zone6schedThuPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x1889 | Zone6schedThuPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x188A | Zone6schedThuPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x188B | Zone6schedThuPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x188C | Zone6schedThuPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x188D | Zone6schedThuPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x188E | Zone6schedThuPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x188F | Zone6schedThuPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x1890 | Zone6schedThuPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1891 | Zone6schedThuPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1892 | Zone6schedThuPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1893 | Zone6schedThuPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x1894 | Zone6schedFriPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x1895 | Zone6schedFriPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x1896 | Zone6schedFriPart1Time | UINT8 | 0 | 95 | 24 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x1897 | Zone6schedFriPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x1898 | Zone6schedFriPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x1899 | Zone6schedFriPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x189A | Zone6schedFriPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x189B | Zone6schedFriPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x189C | Zone6schedFriPart2Time | UINT8 | 0 | 95 | 88 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x189D | Zone6schedFriPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x189E | Zone6schedFriPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x189F | Zone6schedFriPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18A0 | Zone6schedFriPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18A1 | Zone6schedFriPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x18A2 | Zone6schedFriPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18A3 | Zone6schedFriPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18A4 | Zone6schedFriPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18A5 | Zone6schedFriPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18A6 | Zone6schedFriPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18A7 | Zone6schedFriPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x18A8 | Zone6schedFriPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18A9 | Zone6schedFriPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18AA | Zone6schedFriPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18AB | Zone6schedFriPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18AC | Zone6schedFriPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18AD | Zone6schedFriPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18AE | Zone6schedFriPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18AF | Zone6schedFriPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18B0 | Zone6schedFriPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18B1 | Zone6schedFriPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18B2 | Zone6schedFriPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18B3 | Zone6schedFriPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18B4 | Zone6schedFriPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18B5 | Zone6schedFriPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18B6 | Zone6schedFriPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18B7 | Zone6schedFriPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18B8 | Zone6schedSatPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18B9 | Zone6schedSatPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x18BA | Zone6schedSatPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18BB | Zone6schedSatPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18BC | Zone6schedSatPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18BD | Zone6schedSatPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18BE | Zone6schedSatPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18BF | Zone6schedSatPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x18C0 | Zone6schedSatPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18C1 | Zone6schedSatPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18C2 | Zone6schedSatPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18C3 | Zone6schedSatPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18C4 | Zone6schedSatPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18C5 | Zone6schedSatPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x18C6 | Zone6schedSatPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18C7 | Zone6schedSatPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18C8 | Zone6schedSatPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18C9 | Zone6schedSatPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18CA | Zone6schedSatPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18CB | Zone6schedSatPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x18CC | Zone6schedSatPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18CD | Zone6schedSatPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18CE | Zone6schedSatPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18CF | Zone6schedSatPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18D0 | Zone6schedSatPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18D1 | Zone6schedSatPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18D2 | Zone6schedSatPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18D3 | Zone6schedSatPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18D4 | Zone6schedSatPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18D5 | Zone6schedSatPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18D6 | Zone6schedSatPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18D7 | Zone6schedSatPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18D8 | Zone6schedSatPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18D9 | Zone6schedSatPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18DA | Zone6schedSatPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18DB | Zone6schedSatPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18DC | Zone6schedSunPart1Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18DD | Zone6schedSunPart1Label | CHAR | 0 | 32 | awake | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "morning" for Lite.
0x18DE | Zone6schedSunPart1Time | UINT8 | 0 | 95 | 32 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18DF | Zone6schedSunPart1Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18E0 | Zone6schedSunPart1csp | FLOAT | 10 | 32.2 | 22.2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18E1 | Zone6schedSunPart1hsp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18E2 | Zone6schedSunPart2Enabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18E3 | Zone6schedSunPart2Label | CHAR | 0 | 32 | sleep | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "day" for Lite.
0x18E4 | Zone6schedSunPart2Time | UINT8 | 0 | 95 | 92 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18E5 | Zone6schedSunPart2Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18E6 | Zone6schedSunPart2csp | FLOAT | 10 | 32.2 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18E7 | Zone6schedSunPart2hsp | FLOAT | 10 | 32.2 | 17.8 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18E8 | Zone6schedSunPart3Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18E9 | Zone6schedSunPart3Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "evening" for Lite.
0x18EA | Zone6schedSunPart3Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18EB | Zone6schedSunPart3Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18EC | Zone6schedSunPart3csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18ED | Zone6schedSunPart3hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18EE | Zone6schedSunPart4Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled.
0x18EF | Zone6schedSunPart4Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day; Always "night" for Lite.
0x18F0 | Zone6schedSunPart4Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18F1 | Zone6schedSunPart4Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18F2 | Zone6schedSunPart4csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18F3 | Zone6schedSunPart4hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18F4 | Zone6schedSunPart5Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18F5 | Zone6schedSunPart5Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18F6 | Zone6schedSunPart5Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18F7 | Zone6schedSunPart5Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18F8 | Zone6schedSunPart5csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18F9 | Zone6schedSunPart5hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
0x18FA | Zone6schedSunPart6Enabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Set to a '1' when this event in the day's schedule is enabled. (Only 4 schedule events are supporte on the Lite.)
0x18FB | Zone6schedSunPart6Label | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Name of this schedule event for this day;
0x18FC | Zone6schedSunPart6Time | UINT8 | 0 | 95 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Start time for this schedule event, in 15 minute increments
0x18FD | Zone6schedSunPart6Action | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Action for this schedule event to perform; currently always set to '0' for "set temperature". In future may implement '1' for "turn system off" and additional values for other system modes.
0x18FE | Zone6schedSunPart6csp | FLOAT | 10 | 32.2 | 27 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Cooling setpoint for this schedule event in 0.1deg C
0x18FF | Zone6schedSunPart6hsp | FLOAT | 10 | 32.2 | 18 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Heating setpoint for this schedule event in 0.1deg C
//Single zone/Zone 1 schedule selections for system mode and sensors
0x1900 | schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1901 | schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1902 | schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1903 | schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1904 | schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1905 | schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1906 | schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1907 | schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1908 | schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1909 | schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190A | schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190B | schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190C | schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190D | schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190E | schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x190F | schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1910 | schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1911 | schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1912 | schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1913 | schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1914 | schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1915 | schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1916 | schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1917 | schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1918 | schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1919 | schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191A | schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191B | schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191C | schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191D | schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191E | schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x191F | schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1920 | schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1921 | schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1922 | schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1923 | schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1924 | schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1925 | schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1926 | schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1927 | schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1928 | schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1929 | schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x192A | schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x192B | schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x192C | schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x192D | schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x192E | schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x192F | schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1930 | schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1931 | schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1932 | schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1933 | schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1934 | schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1935 | schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1936 | schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1937 | schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1938 | schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1939 | schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193A | schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193B | schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193C | schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193D | schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193E | schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x193F | schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1940 | schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1941 | schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1942 | schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1943 | schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1944 | schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1945 | schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1946 | schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1947 | schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1948 | schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1949 | schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194A | schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194B | schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194C | schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194D | schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194E | schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x194F | schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1950 | schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1951 | schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1952 | schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1953 | schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1954 | schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x1955 | schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1956 | schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1957 | schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1958 | schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1959 | schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195A | schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195B | schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195C | schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195D | schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195E | schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x195F | schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1960 | schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1961 | schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1962 | schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1963 | schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1964 | schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1965 | schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1966 | schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1967 | schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1968 | schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1969 | schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196A | schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196B | schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196C | schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196D | schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196E | schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x196F | schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1970 | schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1971 | schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1972 | schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1973 | schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1974 | schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1975 | schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1976 | schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1977 | schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1978 | schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1979 | schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x197A | schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x197B | schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x197C | schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x197D | schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//Zone 2 schedule selections for system mode and sensors
0x1980 | Zone2schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1981 | Zone2schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1982 | Zone2schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1983 | Zone2schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1984 | Zone2schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1985 | Zone2schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1986 | Zone2schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1987 | Zone2schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1988 | Zone2schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1989 | Zone2schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198A | Zone2schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198B | Zone2schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198C | Zone2schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198D | Zone2schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198E | Zone2schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x198F | Zone2schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1990 | Zone2schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1991 | Zone2schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1992 | Zone2schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1993 | Zone2schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1994 | Zone2schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1995 | Zone2schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1996 | Zone2schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1997 | Zone2schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1998 | Zone2schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1999 | Zone2schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199A | Zone2schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199B | Zone2schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199C | Zone2schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199D | Zone2schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199E | Zone2schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x199F | Zone2schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A0 | Zone2schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A1 | Zone2schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A2 | Zone2schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A3 | Zone2schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A4 | Zone2schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A5 | Zone2schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A6 | Zone2schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A7 | Zone2schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A8 | Zone2schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19A9 | Zone2schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19AA | Zone2schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x19AB | Zone2schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19AC | Zone2schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19AD | Zone2schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19AE | Zone2schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19AF | Zone2schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B0 | Zone2schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B1 | Zone2schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B2 | Zone2schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B3 | Zone2schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B4 | Zone2schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B5 | Zone2schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B6 | Zone2schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B7 | Zone2schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B8 | Zone2schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19B9 | Zone2schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BA | Zone2schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BB | Zone2schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BC | Zone2schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BD | Zone2schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BE | Zone2schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19BF | Zone2schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C0 | Zone2schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C1 | Zone2schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C2 | Zone2schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C3 | Zone2schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C4 | Zone2schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C5 | Zone2schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C6 | Zone2schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C7 | Zone2schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C8 | Zone2schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19C9 | Zone2schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CA | Zone2schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CB | Zone2schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CC | Zone2schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CD | Zone2schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CE | Zone2schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19CF | Zone2schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D0 | Zone2schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D1 | Zone2schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D2 | Zone2schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D3 | Zone2schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D4 | Zone2schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x19D5 | Zone2schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D6 | Zone2schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D7 | Zone2schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D8 | Zone2schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19D9 | Zone2schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DA | Zone2schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DB | Zone2schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DC | Zone2schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DD | Zone2schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DE | Zone2schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19DF | Zone2schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E0 | Zone2schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E1 | Zone2schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E2 | Zone2schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E3 | Zone2schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E4 | Zone2schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E5 | Zone2schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E6 | Zone2schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E7 | Zone2schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E8 | Zone2schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19E9 | Zone2schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19EA | Zone2schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19EB | Zone2schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19EC | Zone2schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19ED | Zone2schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19EE | Zone2schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19EF | Zone2schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F0 | Zone2schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F1 | Zone2schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F2 | Zone2schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F3 | Zone2schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F4 | Zone2schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F5 | Zone2schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F6 | Zone2schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F7 | Zone2schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F8 | Zone2schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19F9 | Zone2schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19FA | Zone2schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19FB | Zone2schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19FC | Zone2schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x19FD | Zone2schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//Zone 3 schedule selections for system mode and sensors
0x1A00 | Zone3schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1A01 | Zone3schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A02 | Zone3schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A03 | Zone3schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A04 | Zone3schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A05 | Zone3schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A06 | Zone3schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A07 | Zone3schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A08 | Zone3schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A09 | Zone3schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0A | Zone3schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0B | Zone3schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0C | Zone3schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0D | Zone3schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0E | Zone3schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A0F | Zone3schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A10 | Zone3schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A11 | Zone3schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A12 | Zone3schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A13 | Zone3schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A14 | Zone3schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A15 | Zone3schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A16 | Zone3schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A17 | Zone3schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A18 | Zone3schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A19 | Zone3schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1A | Zone3schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1B | Zone3schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1C | Zone3schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1D | Zone3schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1E | Zone3schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A1F | Zone3schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A20 | Zone3schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A21 | Zone3schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A22 | Zone3schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A23 | Zone3schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A24 | Zone3schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A25 | Zone3schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A26 | Zone3schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A27 | Zone3schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A28 | Zone3schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A29 | Zone3schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A2A | Zone3schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x1A2B | Zone3schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A2C | Zone3schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A2D | Zone3schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A2E | Zone3schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A2F | Zone3schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A30 | Zone3schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A31 | Zone3schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A32 | Zone3schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A33 | Zone3schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A34 | Zone3schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A35 | Zone3schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A36 | Zone3schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A37 | Zone3schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A38 | Zone3schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A39 | Zone3schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3A | Zone3schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3B | Zone3schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3C | Zone3schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3D | Zone3schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3E | Zone3schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A3F | Zone3schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A40 | Zone3schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A41 | Zone3schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A42 | Zone3schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A43 | Zone3schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A44 | Zone3schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A45 | Zone3schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A46 | Zone3schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A47 | Zone3schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A48 | Zone3schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A49 | Zone3schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4A | Zone3schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4B | Zone3schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4C | Zone3schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4D | Zone3schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4E | Zone3schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A4F | Zone3schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A50 | Zone3schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A51 | Zone3schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A52 | Zone3schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A53 | Zone3schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A54 | Zone3schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x1A55 | Zone3schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A56 | Zone3schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A57 | Zone3schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A58 | Zone3schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A59 | Zone3schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5A | Zone3schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5B | Zone3schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5C | Zone3schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5D | Zone3schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5E | Zone3schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A5F | Zone3schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A60 | Zone3schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A61 | Zone3schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A62 | Zone3schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A63 | Zone3schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A64 | Zone3schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A65 | Zone3schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A66 | Zone3schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A67 | Zone3schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A68 | Zone3schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A69 | Zone3schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6A | Zone3schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6B | Zone3schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6C | Zone3schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6D | Zone3schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6E | Zone3schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A6F | Zone3schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A70 | Zone3schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A71 | Zone3schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A72 | Zone3schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A73 | Zone3schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A74 | Zone3schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A75 | Zone3schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A76 | Zone3schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A77 | Zone3schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A78 | Zone3schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A79 | Zone3schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A7A | Zone3schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A7B | Zone3schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A7C | Zone3schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A7D | Zone3schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//Zone 4 schedule selections for system mode and sensors
0x1A80 | Zone4schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1A81 | Zone4schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A82 | Zone4schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A83 | Zone4schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A84 | Zone4schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A85 | Zone4schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A86 | Zone4schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A87 | Zone4schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A88 | Zone4schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A89 | Zone4schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8A | Zone4schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8B | Zone4schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8C | Zone4schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8D | Zone4schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8E | Zone4schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A8F | Zone4schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A90 | Zone4schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A91 | Zone4schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A92 | Zone4schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A93 | Zone4schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A94 | Zone4schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A95 | Zone4schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A96 | Zone4schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A97 | Zone4schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A98 | Zone4schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A99 | Zone4schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9A | Zone4schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9B | Zone4schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9C | Zone4schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9D | Zone4schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9E | Zone4schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1A9F | Zone4schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA0 | Zone4schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA1 | Zone4schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA2 | Zone4schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA3 | Zone4schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA4 | Zone4schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA5 | Zone4schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA6 | Zone4schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA7 | Zone4schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA8 | Zone4schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AA9 | Zone4schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AAA | Zone4schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x1AAB | Zone4schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AAC | Zone4schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AAD | Zone4schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AAE | Zone4schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AAF | Zone4schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB0 | Zone4schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB1 | Zone4schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB2 | Zone4schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB3 | Zone4schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB4 | Zone4schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB5 | Zone4schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB6 | Zone4schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB7 | Zone4schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB8 | Zone4schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AB9 | Zone4schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABA | Zone4schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABB | Zone4schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABC | Zone4schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABD | Zone4schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABE | Zone4schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ABF | Zone4schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC0 | Zone4schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC1 | Zone4schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC2 | Zone4schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC3 | Zone4schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC4 | Zone4schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC5 | Zone4schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC6 | Zone4schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC7 | Zone4schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC8 | Zone4schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AC9 | Zone4schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACA | Zone4schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACB | Zone4schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACC | Zone4schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACD | Zone4schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACE | Zone4schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ACF | Zone4schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD0 | Zone4schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD1 | Zone4schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD2 | Zone4schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD3 | Zone4schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD4 | Zone4schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x1AD5 | Zone4schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD6 | Zone4schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD7 | Zone4schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD8 | Zone4schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AD9 | Zone4schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADA | Zone4schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADB | Zone4schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADC | Zone4schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADD | Zone4schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADE | Zone4schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1ADF | Zone4schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE0 | Zone4schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE1 | Zone4schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE2 | Zone4schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE3 | Zone4schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE4 | Zone4schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE5 | Zone4schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE6 | Zone4schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE7 | Zone4schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE8 | Zone4schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AE9 | Zone4schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AEA | Zone4schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AEB | Zone4schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AEC | Zone4schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AED | Zone4schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AEE | Zone4schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AEF | Zone4schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF0 | Zone4schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF1 | Zone4schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF2 | Zone4schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF3 | Zone4schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF4 | Zone4schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF5 | Zone4schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF6 | Zone4schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF7 | Zone4schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF8 | Zone4schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AF9 | Zone4schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AFA | Zone4schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AFB | Zone4schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AFC | Zone4schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1AFD | Zone4schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//Zone 5 schedule selections for system mode and sensors
0x1B00 | Zone5schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1B01 | Zone5schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B02 | Zone5schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B03 | Zone5schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B04 | Zone5schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B05 | Zone5schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B06 | Zone5schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B07 | Zone5schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B08 | Zone5schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B09 | Zone5schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0A | Zone5schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0B | Zone5schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0C | Zone5schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0D | Zone5schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0E | Zone5schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B0F | Zone5schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B10 | Zone5schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B11 | Zone5schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B12 | Zone5schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B13 | Zone5schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B14 | Zone5schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B15 | Zone5schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B16 | Zone5schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B17 | Zone5schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B18 | Zone5schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B19 | Zone5schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1A | Zone5schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1B | Zone5schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1C | Zone5schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1D | Zone5schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1E | Zone5schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B1F | Zone5schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B20 | Zone5schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B21 | Zone5schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B22 | Zone5schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B23 | Zone5schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B24 | Zone5schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B25 | Zone5schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B26 | Zone5schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B27 | Zone5schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B28 | Zone5schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B29 | Zone5schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B2A | Zone5schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x1B2B | Zone5schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B2C | Zone5schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B2D | Zone5schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B2E | Zone5schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B2F | Zone5schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B30 | Zone5schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B31 | Zone5schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B32 | Zone5schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B33 | Zone5schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B34 | Zone5schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B35 | Zone5schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B36 | Zone5schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B37 | Zone5schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B38 | Zone5schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B39 | Zone5schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3A | Zone5schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3B | Zone5schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3C | Zone5schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3D | Zone5schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3E | Zone5schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B3F | Zone5schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B40 | Zone5schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B41 | Zone5schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B42 | Zone5schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B43 | Zone5schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B44 | Zone5schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B45 | Zone5schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B46 | Zone5schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B47 | Zone5schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B48 | Zone5schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B49 | Zone5schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4A | Zone5schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4B | Zone5schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4C | Zone5schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4D | Zone5schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4E | Zone5schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B4F | Zone5schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B50 | Zone5schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B51 | Zone5schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B52 | Zone5schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B53 | Zone5schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B54 | Zone5schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x1B55 | Zone5schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B56 | Zone5schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B57 | Zone5schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B58 | Zone5schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B59 | Zone5schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5A | Zone5schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5B | Zone5schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5C | Zone5schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5D | Zone5schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5E | Zone5schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B5F | Zone5schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B60 | Zone5schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B61 | Zone5schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B62 | Zone5schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B63 | Zone5schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B64 | Zone5schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B65 | Zone5schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B66 | Zone5schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B67 | Zone5schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B68 | Zone5schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B69 | Zone5schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6A | Zone5schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6B | Zone5schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6C | Zone5schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6D | Zone5schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6E | Zone5schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B6F | Zone5schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B70 | Zone5schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B71 | Zone5schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B72 | Zone5schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B73 | Zone5schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B74 | Zone5schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B75 | Zone5schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B76 | Zone5schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B77 | Zone5schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B78 | Zone5schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B79 | Zone5schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B7A | Zone5schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B7B | Zone5schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B7C | Zone5schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B7D | Zone5schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
//Zone 6 schedule selections for system mode and sensors
0x1B80 | Zone6schedMonPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | System mode; 0: off, 1: heat, 2: cool, 3: auto, 4: emergency heat; 5: fan; 6: dry mode; 9: don't change the current system mode; Copied to the "mode" variable except when the value is '9'.
0x1B81 | Zone6schedMonPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B82 | Zone6schedMonPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B83 | Zone6schedMonPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B84 | Zone6schedMonPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B85 | Zone6schedMonPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B86 | Zone6schedTuePart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B87 | Zone6schedTuePart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B88 | Zone6schedTuePart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B89 | Zone6schedTuePart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8A | Zone6schedTuePart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8B | Zone6schedTuePart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8C | Zone6schedWedPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8D | Zone6schedWedPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8E | Zone6schedWedPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B8F | Zone6schedWedPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B90 | Zone6schedWedPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B91 | Zone6schedWedPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B92 | Zone6schedThuPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B93 | Zone6schedThuPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B94 | Zone6schedThuPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B95 | Zone6schedThuPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B96 | Zone6schedThuPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B97 | Zone6schedThuPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B98 | Zone6schedFriPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B99 | Zone6schedFriPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9A | Zone6schedFriPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9B | Zone6schedFriPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9C | Zone6schedFriPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9D | Zone6schedFriPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9E | Zone6schedSatPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1B9F | Zone6schedSatPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA0 | Zone6schedSatPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA1 | Zone6schedSatPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA2 | Zone6schedSatPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA3 | Zone6schedSatPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA4 | Zone6schedSunPart1Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA5 | Zone6schedSunPart2Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA6 | Zone6schedSunPart3Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA7 | Zone6schedSunPart4Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA8 | Zone6schedSunPart5Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BA9 | Zone6schedSunPart6Mode | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BAA | Zone6schedMonPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | MAC address of RF sensor used for control; only copied to "indoorControlSensorMAC" when the corresponding "sched*SensorAvgMethod" is set to "1" or "2".
0x1BAB | Zone6schedMonPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BAC | Zone6schedMonPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BAD | Zone6schedMonPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BAE | Zone6schedMonPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BAF | Zone6schedMonPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB0 | Zone6schedTuePart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB1 | Zone6schedTuePart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB2 | Zone6schedTuePart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB3 | Zone6schedTuePart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB4 | Zone6schedTuePart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB5 | Zone6schedTuePart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB6 | Zone6schedWedPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB7 | Zone6schedWedPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB8 | Zone6schedWedPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BB9 | Zone6schedWedPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBA | Zone6schedWedPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBB | Zone6schedWedPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBC | Zone6schedThuPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBD | Zone6schedThuPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBE | Zone6schedThuPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BBF | Zone6schedThuPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC0 | Zone6schedThuPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC1 | Zone6schedThuPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC2 | Zone6schedFriPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC3 | Zone6schedFriPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC4 | Zone6schedFriPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC5 | Zone6schedFriPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC6 | Zone6schedFriPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC7 | Zone6schedFriPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC8 | Zone6schedSatPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BC9 | Zone6schedSatPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCA | Zone6schedSatPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCB | Zone6schedSatPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCC | Zone6schedSatPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCD | Zone6schedSatPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCE | Zone6schedSunPart1SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BCF | Zone6schedSunPart2SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD0 | Zone6schedSunPart3SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD1 | Zone6schedSunPart4SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD2 | Zone6schedSunPart5SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD3 | Zone6schedSunPart6SensorMAC | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD4 | Zone6schedMonPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Local (thermostat) or IDU sensor value if "tempHumControlSource"="1"; 1: use one RF sensor (may be added to UI in v3.4 release); 2: average one RF sensor and local (may be added to UI in v3.4 release); 3: average all RF sensors (without local); 4: average all RF sensors and local; 9: don't change the current averaging method or Sensor MAC;
0x1BD5 | Zone6schedMonPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD6 | Zone6schedMonPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD7 | Zone6schedMonPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD8 | Zone6schedMonPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BD9 | Zone6schedMonPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDA | Zone6schedTuePart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDB | Zone6schedTuePart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDC | Zone6schedTuePart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDD | Zone6schedTuePart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDE | Zone6schedTuePart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BDF | Zone6schedTuePart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE0 | Zone6schedWedPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE1 | Zone6schedWedPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE2 | Zone6schedWedPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE3 | Zone6schedWedPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE4 | Zone6schedWedPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE5 | Zone6schedWedPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE6 | Zone6schedThuPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE7 | Zone6schedThuPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE8 | Zone6schedThuPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BE9 | Zone6schedThuPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BEA | Zone6schedThuPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BEB | Zone6schedThuPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BEC | Zone6schedFriPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BED | Zone6schedFriPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BEE | Zone6schedFriPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BEF | Zone6schedFriPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF0 | Zone6schedFriPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF1 | Zone6schedFriPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF2 | Zone6schedSatPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF3 | Zone6schedSatPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF4 | Zone6schedSatPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF5 | Zone6schedSatPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF6 | Zone6schedSatPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF7 | Zone6schedSatPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF8 | Zone6schedSunPart1SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BF9 | Zone6schedSunPart2SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BFA | Zone6schedSunPart3SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BFB | Zone6schedSunPart4SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BFC | Zone6schedSunPart5SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
0x1BFD | Zone6schedSunPart6SensorAvgMethod | UINT8 | 0 | 9 | 9 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE
// New Variables (before 0x3000)
2000 | equipmentSettingsReady | BIT | 0 | 1 | 1 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not ready; 1: ready; Written by CT protocol code when first pass of data collection on the CT bus is complete. Used by UI that displays progress circles until this is set to a "1", after which the unitary equipment settings menus are displayed.
0x2001 | ctCFMrequirement | FLOAT | 0 | 127.5, 0xFFFF | 0xFFFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; See similar variables near 0x4244 id in datamap; 0: not ready; 1: ready;
2010 | ctMainScreenSelection | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED (as of 3.2 release) 0: combined main and adjust screens; 1: legacy main screen with separate adjust screen; 2: (reserved)
2011 | ctFontSize | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: normal; 1: large font; Based on user selection for thermostat UI.
2012 | ctQuietModeHODisplayEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: hide quiet mode settings in HO menus; 1: display Quiet Mode settings in HO menus; Tied to "allow homeowner changes" setting in the Quiet Mode Dealer menus that allows them to prevent the HO from making changes to the Quiet Mode settings, as required by some city noise ordinances.
2013 | mainScreenNavIconDisplayEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If disabled removes navigation icons from bottom of main screen display.
2014 | mainScreenSystemMsgDisplayEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If disabled supresses all system status message from below the room temperature.
2015 | mainScreenIndoorHumDisplayEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If disabled removes indoor humidity from the cycled data displayed above the room temperature.
2016 | mainScreenIndoorAQDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If enabled adds indoor air quality to the cycled data displayed above the room temperature.
2017 | mainScreenOutoorTempDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If enabled adds outdoor temperature to the cycled data displayed above the room temperature.
2018 | mainScreenOutdoorHumDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If enabled adds outdoor humidity to the cycled data displayed above the room temperature.
2019 | mainScreenOutdoorAQDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If enabled adds outdoor air quality to the cycled data displayed above the room temperature.
201A | mainScreenDateTimeDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disable; 1: enable; If enabled adds date and time to the cycled data displayed above the room temperature.
2020 | ctFITQcoolingCapacityRange | UINT8 | 0 | 3,0xFF | 0xFF | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | NOT USED; 0=Off (25-100%); 1=A (70% or more); 2=B (85% or more); 3=C (100%); Is for FitQ furnace board
2021 | ClockDisplayEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: don't show clock; 1: display clock (Used for Daikin One Lite, aka "Mini")
2022 | magneticEncoderPresent | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | 0: FALSE (rotary encoder or no dial); 1: TRUE (legacy magnetic dial). If a thermostat has a magnetic dial VenOS will write a '1' to this variable during boot-up. When this is '0' VenOS will not generate the beep on rotation, and the UI will hide the sound menu.
2023 | lightBarBrightness | UINT8 | 1 | 2 | 2 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1="muted" (legacy); 2="bright" (pure blue and red, 100% brightness); Used to set light pipe brightness level if "lightBarEnabled"=1. Removed ability to change this in the UI from the v3.1 Tstat release.
0x2030 | EquipProtocolMaxCoolSetpoint | FLOAT | 10 | 32.2 | 32.2 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | CSP upper limit from equipment protocol software in Celsius
0x2031 | EquipProtocolMinCoolSetpoint | FLOAT | 10 | 32.2 | 10 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | CSP lower limit from equipment protocol software in Celsius
0x2032 | EquipProtocolMaxHeatSetpoint | FLOAT | 10 | 32.2 | 32.2 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | HSP upper limit from equipment protocol software in Celsius
0x2033 | EquipProtocolMinHeatSetpoint | FLOAT | 10 | 32.2 | 10 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | HSP lower limit from equipment protocol software in Celsius
// One Clean Variables
2100 | oneCleanFanActive | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | OneClean active? 0: No, 1: Yes; UI will change this to '1' when user selects "OneClean"; The CT PIC24 Software will make sure system fan is running when this is Active using oneCleanFanSpeed setting if no other active fan demand; VenOS will change to '0' after oneCleanFanDuration length of time.
0x2101 | oneCleanFanSpeed | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: low, 1: medium, 2: high; Speed to run the fan at during OneClean, if no higher priority fan call exists. Used only by CT PIC 24 software, which selects which fan speed take priority.
0x2102 | oneCleanFanDuration | UINT8 | 0 | 24 | 3 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | hours to run fan for One Clean; Will always be the default (3 hours), with no setting in the UI for the initial release. VenOS controls the timer and action for clearing the "oneCleanFanActive" variable to turn the OneClean request for fan off at the end of the time.
0x2103 | oneCleanAction | UINT8 | 0 | 8 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--for future use;
0x2104 | oneCleanAQITrigger | UINT16 | 0 | 500 | 500 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--for future use;
0x2105 | oneCleanVOCtrigger | UINT16 | 0 | 60000 | 60000 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--for future use;
0x2106 | oneCleanParticleTrigger | UINT16 | 0 | 500 | 500 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--for future use;
0x2107 | oneCleanIndoorFanUnitNumber | UINT8 | 0 | 15,0xFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED--for future use; 0=Unit 0, 1= Unit 1, …, 15=unit 15; Used only for a group of P1P2 units to designate which unit is run during OneClean
0x2108 | P1P2S21OneCleanFanSpeed | UINT8 | 0 | 7 | 5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
0x2110 | P1P2S21FanCirculateSpeed | UINT8 | 0 | 7 | 5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
// Additional ADR variables
0x2200 | adrPriceTriggerEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; 0: disabled; 1: enabled;
0x2201 | adrPriceTrigger | UINT16 | 0 | 999, 0xFFFF | 10 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED IN ACTUAL OpenADR implementation; Price threshhold to trigger adr settings
// OpenADR variables
0x2210 | OpenADRenabled | BIT | 0 | 1 | 1 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Enable automated demand response system. Could be enabled or enabled by user in the thermostat UI, or through cloud from utility program when a user signs up or opts out. Equipment control is done through the 0x4246 ctRatedPowerUpperLimitSupported, 0x4247 ctRatedPowerUpperLimit, 0x4248 ctRatedPowerUpperLimitEnable variables.
0x2211 | OpenADRglobalTempMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Maximum indoor temp during any ADR event in 0.1deg C; The cloud uses this to cancel an ADR event if indoor temperature rises above this value, and it is stored in the datamap for tracking and debugging.
0x2212 | OpenADRglobalTempMin | FLOAT | 10 | 32.2 | 10 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Minimum indoor temp during any ADR event in 0.1deg C. The cloud uses this to cancel an ADR event if indoor temperature drops below this value, and it is stored in the datamap for tracking and debugging.
0x2213 | OpenADRpriceTrigger | FLOAT | 0 | 100 | 4 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | User-set price threshhold for price-based ADR events.
0x2214 | OpenADReventID | CHAR | 0 | 36 | NULL | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Active/Most recently completed ADR event ID
0x2215 | OpenADReventStart | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time that the event starts or is scheduled to start by VenOS including the delay added for the random delay.
0x2216 | OpenADReventStop | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Time that the event is scheduled to stop including the delay added for the random delay.
0x2217 | OpenADReventActualStop | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | The actual stop time of the event. Will usually be the same as the adrEventStop, but could be the time that the user opted out of this single event, or the time this event was canceled by exceeding a global max or min temperature.
0x2218 | OpenADReventTempMax | FLOAT | 10 | 32.2 | 32.2 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Maximum cooling threshold during this ADR event in 0.1deg C; supplied in the event request from the utility.
0x2219 | OpenADReventTempMin | FLOAT | 10 | 32.2 | 10 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Minimum heating threshold during this ADR event in 0.1deg C; supplied in the event request from the utility.
0x221A | OpenADReventPrice | FLOAT | 0 | 100 | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Price of electricity for this event, as received from utility.
0x221B | OpenADReventMaxEnergy | UINT8 | 0 | 100 | 70 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Maximum energy consumption for this event in %, as received from the utility.
0x221C | OpenADRoperationalState | UINT8 | 0 | 12 | 5 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current state of ADR operation; 0: "Idle Normal" Indicates that no DR event is in effect and the HVAC system has no/insignificant energy consumption. 1: "Running Normal" Indicates that no DR event is in effect and the HVAC system is running normal under local control. 2: "Running Curtailed" Indicates that a curtailment type DR event is in effect and system is running in General Curtailment mode 3: "Running Heightened" Indicates that a heightened-operation type of DR event is in effect and system is running in Critical Curtailment mode 4: "Idle Curtailed" Indicates that a curtailment type DR event is in effect and the HVAC system is in off mode. 5: "SGD Error Condition" Indicates that the HVAC system is not operating or is in some way disabled (for example, no response to the grid). 6: "Idle Heightened" Indicates that a heightened-operation type of DR event is in effect and the HVAC system is in off mode. 7 = Unused code. 8 = Unused code. 9 = Unused code. 10 = Unused code. 11 = "Idle, Opted Out" Indicates that the HVAC system is presently opted out of any DR events and the system is in off mode. 12 = "Running, Opted Out" Indicates that the SGD is presently opted out of any DR events and the SGD is operating normal under local control.
0x221D | OpenADRoverrideState | UINT8 | 0 | 1 | 0 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Not in ADR override. 1: In ADR override.
0x221E | OpenADReventLevel | UINT8 | 0 | 3 | 3 | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0 = no Curtailment 1 = General Curtailment, 70% max energy cap 2 = Critical Curtailment, 40% max energy cap 3 = Emergency Curtailment, equipment off
0x221F | OpenADRauxHeatingForceOff | UINT8 | 0 | 1 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0 = Allow aux heating during DR Event; 1 = Disable Aux Heating during DR Event; from CCHP-DR requirements, set by VenOS DR control logic to allow or disable electric heat during DR events; not available in UI as a setting;
0x2220 | OpenADReventOptOut | UINT8 | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: No opt out; 1: User selects to opt out of DR event; Used by UI to indicate the user has approved opting out of a DR event, and used by Skyport Cloud to cancel the event for this thermosat.
0x2221 | OpenADRoperationalStateZoneInt | UINT8 | 0 | 12 | 5 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Same definition as the 0x221C "OpenADRoperationalState" variable, but used in Zone Interface thermostat when this value is coming from the Primary Zone thermostat across the CT bus, vs. the "OpenADRoperationalState" variable that is updated by Skyport. The Skyport value take priority, and this one only used by Zone Interfaces that are not connected to WiFi while the Primary thermostat is.
// Dealer Service variables
0x2300 | dealerAccess | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Permanent dealer services access level. 0: no dealer access; 1: dealer read access; 2: dealer edit access
0x2301 | dealerAccessRequestId | CHAR | 0 | 36 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | UUIDv4 identifying the request
0x2302 | dealerAccessRequestName | CHAR | 0 | 64 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of the Daikin One Cloud Services organization requesting access
0x2303 | dealerAccessRequestPhone | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Phone number of the Daikin One Cloud Services organization requesting access
0x2304 | dealerAccessRequestDuration | UINT16 | 0 | 0xFFFF | 120 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Access duration in minutes being requested by the dealer
0x2305 | dealerAccessRequestTimestamp | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Unix timestamp when dealer access was requested
0x2306 | dealerAccessResponseId | CHAR | 0 | 36 | NULL | TRUE | READWRITE | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | UUIDv4 identifying the request
0x2307 | dealerAccessResponseStatus | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: pending 1: grant 2: deny
0x2308 | dealerAccessGrantId | CHAR | 0 | 36 | NULL | TRUE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | UUIDv4 identifying the request
0x2309 | dealerAccessGrantName | CHAR | 0 | 64 | NULL | TRUE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Name of the Daikin One Cloud Services organization granted access
0x230A | dealerAccessGrantExpires | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Unix timestamp when dealer access grant expires
0x2320 | dealerLogoWebAddress | CHAR | 0 | 64 | NULL | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Web link to the dealer's logo.
// ClimateTalk Equipment Capabilities
3000 | ctSystemCapCool | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
3001 | ctSystemCapHeat | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
3002 | ctSystemCapEmergencyHeat | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
3003 | ctSystemCapCompressorHeat | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable; used with other system capabilities to determine display of HP settings menu with lockouts or balance point.
3004 | ctSystemCapGasHeat | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable; used with other system capabilities to determine display of HP settings menu with lockouts or balance point.
3005 | ctSystemCapElectricHeat | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable; used with other system capabilities to determine display of HP settings menu with lockouts or balance point.
3006 | ctSystemCapHumidification | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
3007 | ctSystemCapDehumidification | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
3008 | ctSystemCapVentilation | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not capable; 1: capable;
// ClimateTalk Outdoor Configuration
3009 | ctOutdoorUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
300A | ctOutdoorControlSoftwareVersion | CHAR | 0 | 15 | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
300B | ctOutdoorInverterSoftwareVersion | CHAR | 0 | 8 | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 8 characters of text; inverter only;
300C | ctOutdoorModelNoCharacter1_15 | CHAR | 0 | 15 | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
300D | ctOutdoorSerialNoCharacter1_15 | CHAR | 0 | 15 | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
300E | ctOutdoorNoofHeatStages | UINT8 | 0 | 15, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Value = Number of Stages, 15 = Variable/Modulating; HP only
300F | ctOutdoorNoofCoolStages | UINT8 | 0 | 15, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Value = Number of Stages 15 = Variable/Modulating
3010 | ctOutdoorDehumidificationCapable | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | For 2-stage, 1: yes; 2: no; For inverter, 1: no; 2: yes;
3011 | ctOutdoorTonnage | UINT8 | 0 | 50, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Tonnage*2, 0xFF = Not Available
// ClimateTalk Outdoor Settings
3012 | ctOutdoorCoolTrimFactorHigh | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter AC/HP. -10% (1) to 10% (11) for 2-stage AC/HP, is only trim factor for 2-stage. -15%, -10%, -5%, 0%, 5%, 10%, 15%; for new Fit AC/HP software (March 2020).
3013 | ctOutdoorCoolTrimFactorInt | UINT8 | 1 | 11,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter AC/HP. -15%, -10%, -5%, 0%, 5%, 10%, 15%, 20%, 30%, Max; for new Fit AC/HP software (March 2020).
3014 | ctOutdoorCoolTrimFactorLow | UINT8 | 1 | 11,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter AC/HP. -15%, -10%, -5%, 0%, 5%, 10%, 15%, 20%, 30%, Max; for new Fit AC/HP software (March 2020).
3015 | ctOutdoorCoolAirflowProfiles | UINT8 | 1 | 4,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: Profile A; 2: Profile B; 3: Profile C; 4: Profile D;
3016 | ctOutdoorCoolBlowerOnDelay | UINT8 | 1 | 5,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 5s; 2: 10s; 3: 20s; 4: 30s; 5: 0s; The '0s' option added ~Feb. 2024. Population of data in "ctODCompressorDCVoltage" may be used to trigger display of the 0s option.
3017 | ctOutdoorCoolBlowerOffDelay | UINT8 | 1 | 5,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 30s; 2: 60s; 3: 90s; 4: 120s; 5: 0s; The '0s' option added ~Feb. 2024. Population of data in "ctODCompressorDCVoltage" may be used to trigger display of the 0s option.
3018 | ctOutdoorDehumidificationEnable | UINT8 | 1 | 5,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | For inverter (NOT new Fit Software), 1: no; 2: yes; for 2-stage, 1: yes; 2: no; new Fit software (March 2020): 1: standard; 2: Off; 3: A; 4: B; 5: C;
3019 | ctOutdoorCoolMaxRPS | UINT16 | 0 | 2000,0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | The minimum value for Max RPS of the compressor. The stored value is RPS*10, must be divided by 10 before display. Inverters only.
301A | ctOutdoorCoolMaxRPSOffset | UINT8 | 1 | 41,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Offset to the Max RPS of the system as set in the UI. Values are indexed from 1 = 0 RPS offset to 41 = 20 RPS offset in 0.5 RPS steps, with 21 = 10 RPS offset being typical; inverters only;
301B | ctOutdoorSetMaxCurrent | UINT8 | 1 | 7,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x00: OFF, 0x01: 40%, 0x02: 50%, 0x03: 60%, 0x04: 70%, 0x05: 80%, 0x06: 90%; not used in phase 1
301C | ctOutdoorVerticalRise | UINT8 | 1 | 3,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x01: Same Level, 0x02: Outdoor Lower, 0x03: Indoor Lower; Removed starting with Fit Gen3 (?).
301D | ctOutdoorSizeofHouse | UINT16 | 300 | 20000,0xFFFF | 0xFFFF | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 500 to 20,000 in 100 increments; stored locally in thermostat for reference.
301E | ctOutdoorHPTrimFactorHigh | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter HP. -10% (1) to 10% (11) for 2-stage HP, is only trim factor for 2-stage. -15%, -10%, -5%, 0%, 5%, 10%, 15%; for new Fit HP software (March 2020).
301F | ctOutdoorHPTrimFactorInt | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter HP.a -15%, -10%, -5%, 0%, 5%, 10%, 15%; for new Fit HP software (March 2020).
3020 | ctOutdoorHPTrimFactorLow | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for inverter HP. -15%, -10%, -5%, 0%, 5%, 10%, 15%; for new Fit HP software (March 2020).
3021 | ctOutdoorHPBlowerOnDelay | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 5s; 2: 10s; 3: 15s; 4: 0s; The '0s' option added ~Feb. 2024. Population of data in "ctODCompressorDCVoltage" may be used to trigger display of the 0s option.
3022 | ctOutdoorHPBlowerOffDelay | UINT8 | 1 | 5, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 30s; 2: 50s; 3: 70s; 4: 90s; 5 0s; The '0s' option added ~Feb. 2024. Population of data in "ctODCompressorDCVoltage" may be used to trigger display of the 0s option.
3023 | ctOutdoorDefrostInterval | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | When the "ctDefrostIntervalOptionFlag" variable is '0' the selections are: 1: 30m; 2: 60m; 3: 90m; 4: 120m; When the "ctDefrostIntervalOptionFlag" flag is '1', the "ctOutdoorDefrostInterval" the selections are: 1: 2 hr; 2: 6 hr; 3: 12 hr; 4: 24hr; (added in 2025);
3024 | ctOutdoorHeatMaxRPS | UINT16 | 0 | 2000, 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | The minimum value for Max RPS of the compressor. The stored value is RPS*10, must be divided by 10 before display. Inverters only.
3025 | ctOutdoorHeatMaxRPSOffset | UINT8 | 1 | 41, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Offset to the Max RPS of the system as set in the UI. Values are indexed from 1 = 0 RPS offset to 41 = 20 RPS offset in 0.5 RPS steps, with 21 = 10 RPS offset being typical; inverters only;
3026 | ctOutdoorCompressorDelay | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 0s; 2: 5s; 3: 15s; 4: 30s;
3027 | ctOutdoorBoostModeEnable | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on;
3028 | ctOutdoorBoostTemperature | UINT8 | 1 | 9, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: always on; 2: 70°F; 3: 75°F; 4: 80°F; 5: 85°F; 6: 90°F; 7: 95°F; 8: 100°F; 9: 105°F; 16-18 SEER inverter only;
// ClimateTalk Outdoor Status
3029 | ctOutdoorMode | CHAR | 0 | 15 | NULL | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
302A | ctOutdoorCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
302B | ctOutdoorMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
302C | ctOutdoorHeatRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
302D | ctOutdoorCoolRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
302E | ctOutdoorFanRequestedDemandPercentage | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
302F | ctOutdoorDeHumidificationRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
3030 | ctOutdoorRequestedIndoorAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = CFM; With R32 software release pulls from new generic messages (Get Manufacturere Generic Data, bytes 43-44)
3031 | ctOutdoorCompressorRunTime | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Hours. 0xFFFFFFFF: NotAvailable; With R32 software release pulls from new generic messages (Get Manufacturere Generic Data, bytes 40-42)
3032 | ctOutdoorCompressorReductionMode | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x01: off, 0x02: on, 0xFF: Not Available
3033 | ctOutdoorFanRPM | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | inverter except DZ18: value = fan RPM; DZ18: 0 to 3 range; 0xFFFF: not available;
// ClimateTalk Outdoor Sensors
3034 | ctOutdoorAirTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3035 | ctOutdoorCoilTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3036 | ctOutdoorLiquidTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3037 | ctOutdoorDischargeTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3038 | ctOutdoorDefrostSensorTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3039 | ctOutdoorSuctionPressure | INT16 | -1000 | 10000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = pressure in PSI;
303A | ctOutdoorSuctionTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
// ClimateTalk Air Handler Configuration
303B | ctAHUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
303C | ctAHControlSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Up to 15 characters of text written by the IDU.
303D | ctAHModelNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Up to 15 characters of text written by the IDU; Used by the UI to determine the heater kit selections to display.
303E | ctAHSerialNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Up to 15 characters of text written by the IDU.
303F | ctAHElectricHeatKitSize | UINT8 | 0 | 50, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = size in kW; non-EEV models only, displayed only if ctAHnonDVPECHeaterKitExists set to yes; The selection is made using DIP switches on the IDU PCB.
3040 | ctAHIndoorBlowerMotorSizeHP | UINT8 | 3 | 24, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Installed Blower Size; 3: 1/3 HP; 6: 1/2 HP; 9: 3/4 HP; 12: 1 HP; 24: 2 HP; 0xFF = NotAvailable; written by the IDU.
3041 | ctAHHeatONDelay | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = delay in seconds; for display only; written by IDU PCB for non-EEV models.
3042 | ctAHHeatOFFDelay | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = delay in seconds; for display only; written by IDU PCB for non-EEV models.
// ClimateTalk Air Handler Settings
3043 | ctAHElectricHeatKitWattage | UINT8 | 1 | 8, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | DV25PEC, DV24FEC, DFVE24B, DMVE24B, AHVE24B, or AVPEC25--1: none; 2: 3kW; 3: 5kW; 4: 6kW; 5: 8kW; 6: 10kW; (7: 10kW; 8: 10kW;) DV35FEC, DV36FEC, DV37PEC, DV42FEC, DFVE35C, DFVE36C, DFVE42C, DMVE36C, AHVE35C, AHVE36C, AHVE42C, or AVPEC37--1: none; 2: 5kW; 3: 6kW; 4: 8kW; 5: 10kW; 6: 15kW; 7: 19kW; (8: 19kW;) DV59PEC, DV47FEC, DV48FEC, DFVE47D, DFVE48D, DMVE48D, AHVE47D, AHVE48D, or AVPEC59--1: none; 2: 5kW; 3: 6kW; 4: 8kW; 5: 10kW; 6: 15kW; 7: 20kW; (8: 20kW;) DV61PEC, DV59FEC, DV60FEC, DFVE60D, DFVE59D, DMVE60D,AHVE60D, AHVE59D, or AVPEC61--1: none; 2: 5kW; 3: 6kW; 4: 8kW; 5: 10kW; 6: 15kW; 7: 20kW; 8: 25kW;
3044 | ctAHElectricHeatTrim | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | EEV AHUs; 1: 0%; 2: 2%; 3: 4%; 4: 6%; 5: 8%; 6: 10%; non-EEV AHUs; -10% (1) to 10% (11) in 2% steps.
3045 | ctAHHumidificationSetting | UINT8 | 1 | 3, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; 3: independent; only displays when "humidifier" selected for humidifier relay; for EEV AHUs only;
3046 | ctAHHumidificationFanSpeedPercent | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 25%; 2: 50%; 3: 75%; 4: 100%; only displays when "humidifier" selected for humidifier relay; EEV AHUs only;
3047 | ctAHAccessorySetting | UINT8 | 1 | 3, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | humidifier relay; 1: humidifier; 2: enable with blower; 3: none; non-EEV AHUs only. ;
3048 | ctAHAUXAlarm | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; non-EEV air handlers only;
// ClimateTalk Air Handler Status
3049 | ctAHMode | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
304A | ctAHCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
304B | ctAHMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
304C | ctAHHeatRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
304D | ctAHFanRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
304E | ctAHHumidificationRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
304F | ctAHDehumidificationRequestedDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
3050 | ctAHCurrentIndoorAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = CFM;
3051 | ctAHHeatCurrentDemandStatus | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
3052 | ctAHFanCurrentDemandStatus | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; divide by 2 before display;
3053 | ctAHRefrigerantType | CHAR | 0 | 6 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
3054 | ctAHSuperHeatValue | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3055 | ctAHSubCoolValue | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3056 | ctAHFanRuntime | UINT32 | 0 | 0xFFFFFFFF | 0xFFFFFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = runtime in hours;
3057 | ctAHLiquidTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3058 | ctAHSuctionTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
3059 | ctAHPressureSensor | INT16 | -1000 | 10000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = pressure in PSI;
305A | ctAHLiquidGasTemperature | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; divide by 10 before display;
// ClimateTalk Furnace Configuration
305B | ctIFCUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
305C | ctIFCControlSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
305D | ctIFCModelNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
305E | ctIFCSerialNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
305F | ctIFCNoofGasHeatStages | UINT8 | 0 | 15, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Value = Number of Stages 15= Variable/Modulating
3060 | ctIFCFurnaceSize | UINT8 | 0 | 120, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Furnace Size in KBTU; 0xFF = NotAvailable
3061 | ctIFCBlowerMotorSizeHP | UINT8 | 0 | 24, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Installed Blower Size; 3: 1/3 HP; 6: 1/2 HP; 9: 3/4 HP; 12: 1 HP; 24: 2 HP; 0xFF = NotAvailable
// ClimateTalk Furnace Settings
3062 | ctIFCGasHeatTrimFactorPercent | UINT8 | 1 | 17, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (=1) to 15% (=11) in 3% steps for R410A mod furnaces. -10% (=1) to 10% (=M85511) for R410A 2-stage furnaces. -16% (=1) to 16% (=17) in 2% steps for R32 furnaces.
3063 | ctIFCGasHeatOnDelay | UINT8 | 1 | 6, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 5s; 2: 10s; 3: 15s; 4: 20s: 5: 25s; 6: 30s
3064 | ctIFCGasHeatOffDelay | UINT8 | 1 | 6, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 30s; 2: 60s; 3: 90s; 4: 120s; 5: 150s; 6: 180s
3065 | ctIFCHeatAirflowProfile | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: Tap 1; 2: Tap B; 3: Tap C; 4: Tap D;
3066 | ctIFCAUXAlarm | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: on; 2: off; Intended for float switch; only 2-stage furnaces have this setting;
3067 | ctIFCHumiditySetting | UINT8 | 1 | 3, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: on with heat and hum; 2: off; 3: on with hum (independent); only 2-stage furnaces have this setting;
3068 | ctIFCHumidityFanSpeed | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 25% fan; 2: 50%; 3: 75%; 4: 100%; only 2-stage furnaces have this setting;
// ClimateTalk Furnace 24VAC Settings
3069 | ctIFC24ACExists | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: exists
306A | ctIFCCoolOffDelayNonCT | UINT8 | 1 | 5, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | If modulating furnace, 1: 30s; 2: 60s; 3: 90s; 4: 120s; (5: 120s) If 2-stage furnace, 1: 0s; 2: 30s; 3: 60s; 4: 90s; 5: 120s;
306B | ctIFCCoolOnDelayNonCT | UINT8 | 1 | 5, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | If modulating furnace, 1: 5s; 2: 10s; 3: 20s; 4: 30s; (5: 30s) If 2-stage furnace, 1: 1s; 2: 5s; 3: 10s; 4: 20s; 5: 30s;
306C | ctIFCCoolAirflowProfileNonCT | UINT8 | 1 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: Profile A; 2: Profile B; 3: Profile C; 4: Profile D;
306D | ctIFCCoolAirflowTrimNonCT | UINT8 | 1 | 11, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | -15% (1) to 15% (11) in 3% steps for 24VAC in mod furnace. -10% (1) to 10% (11) for 24VAC in 2-stage furnace.
306E | ctIFCCoolCFMNonCT | UINT8 | 1 | 7, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: 18kBTU; 2: 24kBTU; 3: 30kBTU; 4: 36kBTU; 5: 42kBTU; 6: 48kBTU; 7: 60kBTU;
// ClimateTalk Furnace Status
306F | ctIFCOperatingHeatCoolMode | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
3070 | ctIFCCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
3071 | ctIFCMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
3072 | ctIFCFanRequestedDemandPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3073 | ctIFCHeatRequestedDemandPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3074 | ctIFCCoolRequestedDemandPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3075 | ctIFCHumRequestedDemandPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3076 | ctIFCDehumRequestedDemandPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3077 | ctIFCIndoorBlowerAirflow | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = CFM;
3078 | ctIFCCurrentHeatActualStatus | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
3079 | ctIFCCurrentCoolActualStatus | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
307A | ctIFCCurrentFanActualStatus | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2;
//ClimateTalk Coil configuration
307B | ctCoilUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
307C | ctCoilControlSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
307D | ctCoilSerialNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 15 characters of text
//Aux Humidifier settings
307E | ctHumidifierConnection | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: Aux 1; 2: Aux 2;
307F | ctHumidifierControl | UINT8 | 1 | 3 | 2 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1: On with heat; 2: On with heat and hum; 3: On with hum;
3080 | ctHumidifierNumPads | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0, 1, 2;
//Aux Dehumidifier settings
3081 | ctDehumidifierConnection | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: Aux 1; 2: Aux 2;
3082 | ctDehumidifierControl | UINT8 | 1 | 4 | 2 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1: On with cool; 2: On with cool and dehum; 3: On with dehum; 4: On with no cool and dehum; Only options 1 and 2 will be supported for initial P1P2/S21 release of aux dehum;
3083 | ctDehumidifierFanSpeed | UINT8 | 0 | 200 | 200 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: 0%; 50: 25%; 100: 50%, 150: 75%; 200: 100%;
//Other Added Equipment
3084 | NumUVBulbs | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | value = number of bulbs;
3085 | NumHEPAfilters | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | value = number of filters;
3086 | NumMediafilters | UINT8 | 0 | 2 | 1 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | value = number of filters; default is 1, since every system should have at least 1 filter.
3087 | NumElectronicfilters | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | value = number of filters;
3088 | ctZoneBoardExists | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: exists
//ClimateTalk System Test
3089 | ctOutdoorSystemVerificationTest | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it. Only supported by inverter equipment, ODU will end test after about 11 minutes unless manually stopped. Must be started with OFF system mode.
308A | ctOutdoorChargeMode | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it. With R32 release is also used for new Charge Verification Test, which will run System Test before starting if needed.
308B | ctSysTestCool | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
308C | ctSysTestFan | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
308D | ctSysTestHeatPumpHeat | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
308E | ctSysTestGasHeat | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
308F | ctSysTestElectricHeat | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
3090 | ctSysTestHumidifier | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
3091 | ctSysTestDehumidifier | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it.
3092 | ctOutdoorPumpDown | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it. Only supported by non-Fit inverter equipment.
3093 | ctOutdoorForceDefrost | UINT8 | 0 | 2, 0xFF | 0xFF | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Planned for v2.9 OTA release; 0: not run; 1: stopped; 2: running; 0xFF: not available; 0 not used, 1 written by protocol software if equipment capable of the test. A non-0xFF value triggers the UI to display it. ODU will turn test for up to 10 minutes.
// ClimateTalk Tstat Configuration
3094 | ctStatControlID | UINT16 | 0 | 0xFFFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; To be assigned by Daikin
3095 | ctStatUnitType | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0x00: Reserved, 0x01: Daikin, 0x02: Venstar, 0x03: Gas Furnace, 0x04: Air Handler, 0x05: Air Conditioner, 0x06: Heat Pump, 0x07: EEV, 0x08: Humidifier, 0x09: De-Humidifier, 0x0A: Ventilator, 0x0B: Air Cleaner, 0x0C: Zone Controller, 0x12: Unitary Control, 0x16: Zone interface (wired zone thermostat), 0x25: Zone Damper (zone board), 0xFF: Not Available, 0xFE: Test Equipment;
3096 | ctStatCTSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | The ClimateTalk PIC24 software version; 15 characters of text, populated starting in the v3.6 release.
3097 | ctStatOSSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; 15 characters of text
3098 | ctStatUISoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | UI software version, populated starting in v3.6 thermostat release; may be used to pull correct UI version into the homeowner app, DOCS app, and website.
3099 | ctStatModelNoCharacter1_15 | CHAR | 0 | 32 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; "statModel" variable used instead.
309A | ctStatSerialNoCharacter1_15 | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Started to be used to program thermostat serial number, possibly in middle of 2021?
// ClimateTalk Tstat Settings
309B | ctStatBalancePoint | UINT8 | 0 | 0xFF | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; For possible future use
309C | ctStatHighStageHeatDifferential | UINT8 | 0 | 0xFF | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; For possible future use
309D | ctStatHighStageHeatTimer | UINT8 | 0 | 0xFF | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; For possible future use
// ClimateTalk Tstat Status
309E | ctStatCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used to report critical faults generated within the thermostat.
309F | ctStatMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used to report minor faults generated within the thermostat.
// Commission Settings
30A0 | commissionStatus | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not commissioned, 1: commissioned, 2: decommissioned; If set to '0' UI will start at Daikin Welcome screen when enter commissioning menus; If '1' will start at setup screen; '2' not used;
30A1 | commissionPersonalization | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not started, 1: completed, 2: not used yet; A '0' means the installer hasn't entered this comissioning step yet, a '1' will mark this step with a green check mark in the UI;
30A2 | commissionCommunication | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not started, 1: completed, 2: not used yet; A '0' means the installer hasn't entered this comissioning step yet, a '1' will mark this step with a green check mark in the UI;
30A3 | commissionEquipment | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not started, 1: completed, 2: not used yet; A '0' means the installer hasn't entered this comissioning step yet, a '1' will mark this step with a green check mark in the UI;
30A4 | commissionOptimization | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not started, 1: completed, 2: not used yet; A '0' means the installer hasn't entered this comissioning step yet, a '1' will mark this step with a green check mark in the UI;
30A5 | commissionPreferences | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: not started, 1: completed, 2: not used yet; A '0' means the installer hasn't entered this comissioning step yet, a '1' will mark this step with a green check mark in the UI;
// GUI Settings
30A6 | alertCustom1Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Name of the custom alert
30A7 | alertCustom1Description | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Description of the custom alert
30A8 | alertCustom1Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Calendar date on which to receive custom alert
30A9 | alertCustom1Repeat | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Repeat the custom reminder every year
30AA | alertCustom1Active | BIT | 0 | 1 | 0 | TRUE | READ | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Custom alert is triggered
30AB | alertCustom2Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Name of the custom alert
30AC | alertCustom2Description | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Description of the custom alert
30AD | alertCustom2Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Calendar date on which to receive custom alert
30AE | alertCustom2Repeat | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Repeat the custom reminder every year
30AF | alertCustom2Active | BIT | 0 | 1 | 0 | TRUE | READ | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Custom alert is triggered
30B0 | alertCustom3Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Name of the custom alert
30B1 | alertCustom3Description | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Description of the custom alert
30B2 | alertCustom3Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Calendar date on which to receive custom alert
30B3 | alertCustom3Repeat | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Repeat the custom reminder every year
30B4 | alertCustom3Active | BIT | 0 | 1 | 0 | TRUE | READ | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Custom alert is triggered
30B5 | alertCustom4Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Name of the custom alert
30B6 | alertCustom4Description | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Description of the custom alert
30B7 | alertCustom4Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Calendar date on which to receive custom alert
30B8 | alertCustom4Repeat | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Repeat the custom reminder every year
30B9 | alertCustom4Active | BIT | 0 | 1 | 0 | TRUE | READ | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED;
30BA | alertCustom5Name | CHAR | 0 | 32 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Name of the custom alert
30BB | alertCustom5Description | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Description of the custom alert
30BC | alertCustom5Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Calendar date on which to receive custom alert
30BD | alertCustom5Repeat | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Repeat the custom reminder every year
30BE | alertCustom5Active | BIT | 0 | 1 | 0 | TRUE | READ | READ | NONE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Custom alert is triggered
30BF | messageHistory1Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30C0 | messageHistory1Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30C1 | messageHistory1Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30C2 | messageHistory2Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30C3 | messageHistory2Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30C4 | messageHistory2Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30C5 | messageHistory3Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30C6 | messageHistory3Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED;
30C7 | messageHistory3Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30C8 | messageHistory4Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30C9 | messageHistory4Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30CA | messageHistory4Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30CB | messageHistory5Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30CC | messageHistory5Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30CD | messageHistory5Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30CE | messageHistory6Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30CF | messageHistory6Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30D0 | messageHistory6Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30D1 | messageHistory7Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30D2 | messageHistory7Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30D3 | messageHistory7Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30D4 | messageHistory8Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30D5 | messageHistory8Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30D6 | messageHistory8Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30D7 | messageHistory9Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30D8 | messageHistory9Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30D9 | messageHistory9Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30DA | messageHistory10Date | UINT32 | 0 | 0xFFFFFFFF | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Timestamp when the message was shown
30DB | messageHistory10Type | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Message Type: 0: alert, 1: reminder, 2: tip
30DC | messageHistory10Text | CHAR | 0 | 256 | NULL | TRUE | READWRITE | READ | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; Text contents of the message
30DD | tipWifiShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been shown the Wifi tip
30DE | tipAccountShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been show the Account tip
30DF | tipGeofencingShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been shown the Geofencing tip
30E0 | tipScheduleShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been shown the Schedule tip
30E1 | tipAutoModeShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been shown the AutoMode tip
30E2 | tipAirCirculationShown | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | NONE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED; The user has been shown the AirCirculation tip
// ClimateTalk Control Algorithm % demand
3100 | ctControlAlgorithmCoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
3101 | ctControlAlgorithmOvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
3102 | ctControlAlgorithmHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
3103 | ctControlAlgorithmAuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
3104 | ctControlAlgorithmBackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
3105 | ctControlAlgorithmHumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
3106 | ctControlAlgorithmDehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
3107 | ctControlAlgorithmFanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
3108 | ctControlAlgorithmRawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3110 | Zone2CoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3111 | Zone2OvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
0x3112 | Zone2HeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3113 | Zone2AuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3114 | Zone2BackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3115 | Zone2HumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3116 | Zone2DehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3117 | Zone2FanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3118 | Zone2RawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3120 | Zone3CoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3121 | Zone3OvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
0x3122 | Zone3HeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3123 | Zone3AuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3124 | Zone3BackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3125 | Zone3HumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3126 | Zone3DehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3127 | Zone3FanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3128 | Zone3RawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3130 | Zone4CoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3131 | Zone4OvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
0x3132 | Zone4HeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3133 | Zone4AuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3134 | Zone4BackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3135 | Zone4HumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3136 | Zone4DehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3137 | Zone4FanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3138 | Zone4RawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3140 | Zone5CoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3141 | Zone5OvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
0x3142 | Zone5HeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3143 | Zone5AuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3144 | Zone5BackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3145 | Zone5HumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3146 | Zone5DehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3147 | Zone5FanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3148 | Zone5RawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3150 | Zone6CoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3151 | Zone6OvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling
0x3152 | Zone6HeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3153 | Zone6AuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3154 | Zone6BackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3155 | Zone6HumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3156 | Zone6DehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3157 | Zone6FanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3158 | Zone6RawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3160 | zoningControlAlgorithmCoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Cool demand calculated by CT control algorithm and sent to equipment
0x3161 | zoningControlAlgorithmOvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Overcool demand calculated by CT control algorithm and used internally to indicate active overcooling; May not make sense for overall system.
0x3162 | zoningControlAlgorithmHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Heat demand calculated by CT control algorithm and sent to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3163 | zoningControlAlgorithmAuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Aux heat demand calculated by CT control algorithm and sent to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3164 | zoningControlAlgorithmBackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Back-up heat demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output, when in Emergency Heat mode.
0x3165 | zoningControlAlgorithmHumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Hum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3166 | zoningControlAlgorithmDehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Dehum demand calculated by CT control algorithm and sent to equipment and/or used to turn on an aux output
0x3167 | zoningControlAlgorithmFanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; fan demand calculated by CT control algorithm and sent to equipment to turn on the fan
0x3168 | zoningControlAlgorithmRawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; raw demand calculated by CT control algorithm and used in calculating the other demand percentages.
0x3170 | zoningControlTotalCoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total cool demand calculated by CT control algorithm BEFORE deicde what to send to equipment;
0x3171 | zoningControlTotalOvercoolDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total overcool demand calculated by CT control algorithm and used internally to indicate active overcooling; May not make sense for overall system.
0x3172 | zoningControlTotalHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total heat demand calculated by CT control algorithm and BEFORE decide what send to equipment to turn on the compressor, or to turn on the gas furnace or heater strip if there is no HP.
0x3173 | zoningControlTotalAuxHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total aux heat demand calculated by CT control algorithm BEFORE decide what to send to equipment to turn on the heater strip or gas furnace and/or used to turn on an aux output
0x3174 | zoningControlTotalBackupHeatDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total back-up heat demand calculated by CT control algorithm BEFORE decide what to send to equipment and/or to turn on an aux output, when in Emergency Heat mode.
0x3175 | zoningControlTotalHumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total hum demand calculated by CT control algorithm BEFORE decide what to send to equipment and/or to turn on an aux output
0x3176 | zoningControlTotalDehumDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total dehum demand calculated by CT control algorithm BEFORE decide what to send to equipment and/or to turn on an aux output
0x3177 | zoningControlTotalFanDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total fan demand calculated by CT control algorithm BEFORE decide what to send to equipment to turn on the fan;
0x3178 | zoningControlTotalRawDemand | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | demand% * 2; Total raw demand calculated by CT control algorithm BEFORE decide what to send to equipment, and used in calculating the other demand percentages. May not make sense for overall system.
// ClimateTalk Coil and Furnace Status
4000 | ctEEVCoilCriticalFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
4001 | ctEEVCoilMinorFault | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Hex value = error code, as reported by equipment
4002 | ctEEVCoilSuperHeatValue | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10;
4003 | ctEEVCoilSubCoolValue | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10;
4004 | ctEEVCoilLiquidTemperature | INT16 | -1000 | 4000,0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10;
4005 | ctEEVCoilSuctionTemperature | INT16 | -1000 | 4000,0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10;
4006 | ctEEVCoilPressureSensor | INT16 | -1000 | 10000,0x7FFF | 0x7FFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | value = pressure in PSI;
4007 | ctEEVRefrigerantType | UINT8 | 0 | 254, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 = R410A, 1 = R32; from CT generic message; 0xFF = information not available; new with R32 EEV coils;
4010 | ctIFCReturnAirTemperature | INT16 | -4000 | 25000,0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED? (temp in °F)*100; Apparently not populated by furnaces.
4011 | ctIFCSupplyAirTemperature | INT16 | -4000 | 25000,0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED? (temp in °F)*100; Apparently not populated by furnaces.
4012 | ctIFCBoardAirTemperature | INT16 | -4000 | 25000,0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED? (temp in °F)*100; Apparently not populated by furnaces.
4013 | ctIFCFlameStatus | UINT8 | 0 | 2,0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED? 0:None 1:Weak 2:Strong; Apparently not populated by furances.
// IAQ History
0x4020 | IAQDeviceID | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Populated by Skyport for automatically adding an IAQ sensor to the equipment list shown in the thermostat.
0x4021 | IAQhistoryEndDate | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Most recent Unix time at which the IAQ history for the last 24 hours and 7 days was calculated. Intended to be used to show how old data in IAQ history is.
0x4022 | IAQIndoorTimeStamp | UINT32 | 0 | 0xFFFFFFFF | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Unix time of receipt of the most recent real-time IAQ data from sensor.
0x4030 | aqIndoorVOCValueHour1Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4031 | aqIndoorVOCValueHour1Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4032 | aqIndoorParticlesValueHour1Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4033 | aqIndoorParticlesValueHour1Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4034 | aqIndoorVOCValueHour2Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4035 | aqIndoorVOCValueHour2Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4036 | aqIndoorParticlesValueHour2Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4037 | aqIndoorParticlesValueHour2Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4038 | aqIndoorVOCValueHour3Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4039 | aqIndoorVOCValueHour3Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x403A | aqIndoorParticlesValueHour3Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x403B | aqIndoorParticlesValueHour3Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x403C | aqIndoorVOCValueHour4Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x403D | aqIndoorVOCValueHour4Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x403E | aqIndoorParticlesValueHour4Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x403F | aqIndoorParticlesValueHour4Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4040 | aqIndoorVOCValueHour5Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4041 | aqIndoorVOCValueHour5Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4042 | aqIndoorParticlesValueHour5Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4043 | aqIndoorParticlesValueHour5Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4044 | aqIndoorVOCValueHour6Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4045 | aqIndoorVOCValueHour6Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4046 | aqIndoorParticlesValueHour6Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4047 | aqIndoorParticlesValueHour6Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4048 | aqIndoorVOCValueHour7Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4049 | aqIndoorVOCValueHour7Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x404A | aqIndoorParticlesValueHour7Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x404B | aqIndoorParticlesValueHour7Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x404C | aqIndoorVOCValueHour8Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x404D | aqIndoorVOCValueHour8Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x404E | aqIndoorParticlesValueHour8Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x404F | aqIndoorParticlesValueHour8Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4050 | aqIndoorVOCValueHour9Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4051 | aqIndoorVOCValueHour9Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4052 | aqIndoorParticlesValueHour9Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4053 | aqIndoorParticlesValueHour9Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4054 | aqIndoorVOCValueHour10Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4055 | aqIndoorVOCValueHour10Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4056 | aqIndoorParticlesValueHour10Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4057 | aqIndoorParticlesValueHour10Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4058 | aqIndoorVOCValueHour11Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4059 | aqIndoorVOCValueHour11Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x405A | aqIndoorParticlesValueHour11Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x405B | aqIndoorParticlesValueHour11Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x405C | aqIndoorVOCValueHour12Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x405D | aqIndoorVOCValueHour12Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x405E | aqIndoorParticlesValueHour12Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x405F | aqIndoorParticlesValueHour12Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4060 | aqIndoorVOCValueHour13Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4061 | aqIndoorVOCValueHour13Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4062 | aqIndoorParticlesValueHour13Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4063 | aqIndoorParticlesValueHour13Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4064 | aqIndoorVOCValueHour14Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4065 | aqIndoorVOCValueHour14Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4066 | aqIndoorParticlesValueHour14Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4067 | aqIndoorParticlesValueHour14Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4068 | aqIndoorVOCValueHour15Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4069 | aqIndoorVOCValueHour15Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x406A | aqIndoorParticlesValueHour15Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x406B | aqIndoorParticlesValueHour15Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x406C | aqIndoorVOCValueHour16Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x406D | aqIndoorVOCValueHour16Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x406E | aqIndoorParticlesValueHour16Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x406F | aqIndoorParticlesValueHour16Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4070 | aqIndoorVOCValueHour17Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4071 | aqIndoorVOCValueHour17Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4072 | aqIndoorParticlesValueHour17Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4073 | aqIndoorParticlesValueHour17Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4074 | aqIndoorVOCValueHour18Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4075 | aqIndoorVOCValueHour18Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4076 | aqIndoorParticlesValueHour18Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4077 | aqIndoorParticlesValueHour18Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4078 | aqIndoorVOCValueHour19Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4079 | aqIndoorVOCValueHour19Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x407A | aqIndoorParticlesValueHour19Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x407B | aqIndoorParticlesValueHour19Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x407C | aqIndoorVOCValueHour20Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x407D | aqIndoorVOCValueHour20Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x407E | aqIndoorParticlesValueHour20Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x407F | aqIndoorParticlesValueHour20Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4080 | aqIndoorVOCValueHour21Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4081 | aqIndoorVOCValueHour21Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4082 | aqIndoorParticlesValueHour21Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4083 | aqIndoorParticlesValueHour21Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4084 | aqIndoorVOCValueHour22Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4085 | aqIndoorVOCValueHour22Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4086 | aqIndoorParticlesValueHour22Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4087 | aqIndoorParticlesValueHour22Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4088 | aqIndoorVOCValueHour23Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4089 | aqIndoorVOCValueHour23Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x408A | aqIndoorParticlesValueHour23Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x408B | aqIndoorParticlesValueHour23Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x408C | aqIndoorVOCValueHour24Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x408D | aqIndoorVOCValueHour24Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x408E | aqIndoorParticlesValueHour24Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x408F | aqIndoorParticlesValueHour24Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4090 | aqIndoorVOCValueDay1Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4091 | aqIndoorVOCValueDay1Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4092 | aqIndoorParticlesValueDay1Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4093 | aqIndoorParticlesValueDay1Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4094 | aqIndoorVOCValueDay2Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4095 | aqIndoorVOCValueDay2Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4096 | aqIndoorParticlesValueDay2Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4097 | aqIndoorParticlesValueDay2Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x4098 | aqIndoorVOCValueDay3Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x4099 | aqIndoorVOCValueDay3Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x409A | aqIndoorParticlesValueDay3Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x409B | aqIndoorParticlesValueDay3Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x409C | aqIndoorVOCValueDay4Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x409D | aqIndoorVOCValueDay4Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x409E | aqIndoorParticlesValueDay4Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x409F | aqIndoorParticlesValueDay4Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40A0 | aqIndoorVOCValueDay5Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40A1 | aqIndoorVOCValueDay5Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40A2 | aqIndoorParticlesValueDay5Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40A3 | aqIndoorParticlesValueDay5Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40A4 | aqIndoorVOCValueDay6Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40A5 | aqIndoorVOCValueDay6Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40A6 | aqIndoorParticlesValueDay6Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40A7 | aqIndoorParticlesValueDay6Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40A8 | aqIndoorVOCValueDay7Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40A9 | aqIndoorVOCValueDay7Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor VOCs. See "aqIndoorVOCValue" definition and usage.
0x40AA | aqIndoorParticlesValueDay7Avg | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
0x40AB | aqIndoorParticlesValueDay7Max | UINT16 | 0 | 1000 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Indoor particles. See "aqIndoorParticlesValue" for definition and usage.
// New Variables (after 0x3000)
4100 | ctOutdoorDefrostHeat | UINT8 | 1 | 10,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: always on; 2: 30°F; 3: 35°F; 4: 40°F; 5: 45°F; 6: 50°F; 7: 55°F; 8: 60°F; 9: 65°F; 10: always off; Fit and Fit Gen3 equivalent HPs only.
4101 | ctAHnonDVPECHeaterKitExists | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0:no; 1:yes (non-EEV air handlers only); Used within thermostat only to determine whether to display the size in the "ctAHElectricHeatKitSize" variable, and whether to send aux heat demand requests to the IDU.
4102 | ctAHDVPECModelForHeaterKit | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED 0:--; 1: DV25PEC; 2: DV37PEC; 3: DV59PEC; 4: DV61PEC; Was intended for "additional zone" thermostats in an EWC zoning system, but never implemented since not needed;
4103 | ctZone1orOther | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Zone 1; 1: additional zone; Used by UI to hide most equipment settings in the dealer menus if "additional zone" is selected since the data is not populated.
4104 | ctIAQsensorExists | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: exists; In v2.7 software and before set to "1" when an air quality sensor is added using "add equipment". In the future plan to auto-populate this when an IAQ sensor is connected to a thermostat.
4105 | statModel | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Populated by Skyport as "ONEPLUS" for the Daikin One+, "ONETOUCH" for the Daikin One Touch and Amana; "ONELITE_P1P2S21" for the S21 and VRV versions of the Lite, and "ONELITE_CT" for Goodman volume zone thermostat; "statBrand" must be looked at the same time to determine the unique thermostat model.
4106 | statFirmware | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Populated by Skyport
4107 | statType | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Populated by Skyport
4108 | proximityEnabled | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | NOT USED; Enable use of the proximity sensor which was removed in 2021.
4109 | aqIndoorVOCLevel | UINT8 | 0 | 5 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor air quality level from TZOA "voc_color" telemetry data, limited to values 0, 1, or 2; 0: good, 1: moderate, 2: unhealthy for sensitive groups, 3: unhealthy, 4: very unhealthy, 5: hazardous; From TZOA stream, mimics gov't levels.
410A | aqIndoorParticlesLevel | UINT8 | 0 | 5 | 0 | FALSE | READ | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Current indoor air quality level from TZOA "pm_color" telemetry data, limited to values 0, 1, or 2; 0: good, 1: moderate, 2: unhealthy for sensitive groups, 3: unhealthy, 4: very unhealthy, 5: hazardous; From TZOA stream, mimics gov't levels.
410B | IaqModelNumber | CHAR | 0 | 15 | 0xFF | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 15 characters of ASCII text; populated from initial TZOA setup data stored in Skyport (?)
410C | IaqSerialNumber | CHAR | 0 | 15 | 0xFF | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 15 characters of ASCII text, populated from "id" TZOA telemetry data.
410D | IaqSoftwareVersion | CHAR | 0 | 8 | 0xFF | FALSE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 8 characters of ASCII text; populated from initial TZOA setup data stored in Skyport (?)
4120 | ctOutdoorCtumVersion | UINT16 | 0 | 200,0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Trim step of 3%; 1: Trim step of 5% and 3 new options for dehumidification setting; Derived in the CT code from the number of fan trim settings returned by the Fit unit (11 for old software with 3% steps, 10 for new software with 5% steps); Used by Pic24 CT software to indicate Fit Gen3 software features
4121 | ctDualFuelFurnaceLockoutEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: furnace not locked out; 1: furnace locked out above balance point (that is stored in the "auxHeatLockoutTemp" variable); Tied to "prioritize efficiency" and "prioritize comfort" radio buttons in HO and dealer screens. Only for dual-fuel CT systems starting in v3.2 release.
4122 | ctIFCsoftwareCompatability | UINT8 | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: R410 furnaces; 1: R32 furnace;
4123 | ctDefrostIntervalOptionFlag | BIT | 0 | 1 | 0 | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | When this flag from the equipment is '0': the "ctOutdoorDefrostInterval" variable has values of 1: 30m; 2: 60m; 3: 90m; 4: 120m; When this flag is '1', the "ctOutdoorDefrostInterval" variable has values of 1: 2 hr; 2: 6 hr; 3: 12 hr; 4: 24hr;
4140 | ctSysTestAuxHeater | UINT8 | 0 | 2,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT IMPLEMENTED YET; 0: not run; 1: stopped; 2: running; 0xFF: not available;
4141 | ctSysTestVentilator | UINT8 | 0 | 2,0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT IMPLEMENTED YET; 0: not run; 1: stopped; 2: running; 0xFF: not available;
4142 | statBrand | CHAR | 0 | 15 | NULL | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Populated by VenOS as "DK" for Daikin, "AM" for Amana, or "GM for Goodman; If NULL, UI assumes Daikin brand. Added in v2.7 software to differentiate Daikin Touch and Amana models.
4143 | statDKNnumber | CHAR | 0 | 15 | NULL | TRUE | READ | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | DKN number written to thermostat by VenOS, starting in v3.3 release?
4144 | statUIsoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; using ctStatUISoftwareVersion variable instead.
4145 | statUILibraryVersion | CHAR | 0 | 15 | NULL | FALSE | READWRITE | READ | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used for internal tracking purposes. Started populating in v3.6 release.
4146 | statCTsoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; using ctStatCTSoftwareVersion variable instead.
4147 | statP1P2S21SoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used for internal tracking purposes. Not populated yet.
4148 | statDGConnectSoftwareVersion | CHAR | 0 | 15 | NULL | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Used for internal tracking purposes. Not populated yet.
// Additional Hum, Dehum, and comfort settings
4160 | humEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: humidification disabled; 1: enabled; Tied to "disable humidification" checkbox in HO humidity menu and installer preferences menu. When checked, this variable is set to '0' to disable humidification.
4161 | dehumEnable | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | NOT USED 0: disabled; 1: enabled; may be used to drive display of dehum setpoint eventually.
4162 | P1P2S21usingOvercoolSetpoint | BIT | 0 | 1 | 0 | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | 0: using normal CSP; 1: using overcool CSP; Used by P1P2/S21 software to tell UI when sending a different CSP to equipment to overcool;
4163 | ctHumidifierFanSpeed | UINT8 | 50 | 200 | 200 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 50: 25%; 100: 50%, 150: 75%; 200: 100%;
4164 | P1P2S21AuxDehumidifierFanSpeed | UINT8 | 0 | 7 | 5 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | NOT USED; 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
4165 | P1P2S21AuxHumidifierFanSpeed | UINT8 | 0 | 7 | 5 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | NOT USED; 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
4166 | ctModIFCHumidificationMode | UINT8 | 1 | 3 | 2 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 1: on; 2: off; 3: independent; For R410A mod furnaces and all R32 furnaces (though "independent" option hidden in UI for first R32 furnace release until can fix furnace software to not require fan demand); this variable is used to add control of independent humidification mode implemented in CT PIC24 code. "On" send hum with heat only, "independent" sends hum independent of a heat call but not with cool.
4167 | ctControlBand | FLOAT | 0 | 2 | 0.5 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0C to 2C in 0.5C (1.0 F) steps. Planned for use in a future release after v3.6.
4168 | humEnableOutdoorTemp | FLOAT | -40 | 18.5 | -20.5 | TRUE | READWRITE | READ | READWRITE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Outdoor temperature in C° below which the "disable humidification" checkbox (humEnable variable) takes effect.
4169 | ctTightTempControlEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: use cruise control algorithm with 2F control band; 1: Use ccHP control algorithm with 1F control band from v3.6 public release; Enable for 1F tighter temperature control algorithm which will be retained for all R410A systems in the v3.7 release, and which may be updated in the future. The looser one to meet the CVP test requirements uses the Cruise Control algorithm with 2F band and will be limited to R32 systems, and will be replaced in the future.
// Commercial Mode Settings
4181 | commercialMode | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | For Future use--0: residential; 1: commercial;
4182 | thermostatZoningRole | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0: neutral (acts as Primary); 1: Primary Zone Thermostat (triggers others to become additional zone thermostats/zone interfaces); 2: Additional Zone Thermostat (Zone Interface); Using "ctUnitControlType" variable instead.
//Aux Heater Settings
4200 | AuxHeaterConnection | UINT8 | 0 | 2 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: none; 1: aux relay 1; 2: aux relay 2; Tells protocol software which aux output to drive when the aux heater is turned on. Is selected by installer when an aux heater is added, and this variable triggers the protocol software to write a '1' to modeEmHeatAvailable if the equipment is capable of mechanical (heat pump) heat.
4201 | AuxHeaterControl | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: Secondary 1: Primary; Tells PIC24 control algorithm whether aux heat is the primary or secondary heat source.
4202 | AuxHeaterControlTonSecondaryAux | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: -1.5°C; 1: -2.0°C; 2: -2.5°C; 3: -3.0°C; 4: -3.5°C; 5: -4.0°C; (must be 2.0°C below the AuxHeaterControlToffSecondaryAux setting); This is the "T on" setting when aux heat is the secondary heat source.
4203 | AuxHeaterControlToffSecondaryAux | UINT8 | 0 | 5 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: 0.5°C; 1: 0°C; 2: -0.5°C; 3: -1.0°C; 4: -1.5°C; 5: -2.0°C; (must be 2.0°C above the AuxHeaterControlTonSecondaryAux setting); This is the "T off" setting when aux heat is the secondary heat source.
4204 | AuxHeaterSetPointGap | UINT8 | 0 | 4 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: -1.0°C; 1: -2.0°C; 2: -3.0°C; 3: -4.0°C; 4: -5.0°C; The is the setpoint gap for sending a lower heat setpoint to the heat pump when aux heat is the primary heat source.
4205 | AuxHeaterIndoorFanEnable | UINT8 | 0 | 1,0xFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0=Off, 1=On; Set by the installed if IDU fan is enabled during an aux heat call; Only available in CT up to v2.8 release.
4206 | AuxHeaterIndoorFanUnitNumber | UINT8 | 0 | 15,0xFF | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED; 0=Unit 0, 1= Unit 1, …, 15=unit 15; P1P2 only; may be used in future to specify which indoor unit fan to run for a group of indoor units, if fan is enabled for aux heat. Without this the fans for all indoor units in a group will be run during aux heat.
4207 | AuxHeaterIndoorFanOnDelay | UINT8 | 0 | 30,0xFF | 3 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | multiplied by 10 to get time in seconds; values are 0, 3=30s, 6=60s, 12=120s, 18=180s, 24=240s, 30=300s; Delay time for when the field setting for leaving on the fan in heat mode is written.
4208 | AuxHeaterIndoorFanOffDelay | UINT8 | 0 | 18,0xFF | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | multiplied by 10 to get time in seconds; values are 0, 1=10s, 3=30s, 6=60s, 9=90s, 12=120s, 18=180s; Delay time for when the field setting is written for turning off the fan for thermo off in heat mode.
4209 | AuxHeaterIndoorFanSpeed | UINT8 | 0 | 2 | 2 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0=low; 1=medium; 2=high; only the CT protocol control software uses this aux heat fan speed variable;
420A | AuxHeaterControlTonPrimaryAux | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: -0.5°C; 1: -1.0°C' (if AuxHeaterControl = '1: Primary'); This is the "T on" setting for when aux heat is the primary heat source.
420B | AuxHeaterControlToffPrimaryAux | UINT8 | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: 0.5°C; 1: (not used); This is the "T off" setting for when aux heat is the primary heat source.
420C | AuxHeaterHeatPumpLockout | FLOAT | -40 | 18.5 | -20.5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Minimum outdoor temperature in C° required to operate the heat pump (Only used by S21 or P1P2. Unitary uses the common HP lockout stored in the "heatPumpLockoutTemp" variable.)
420D | AuxHeaterLockout | FLOAT | -34.5 | 24 | 10 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Maximum outdoor temperature in C° to operate the aux heater connected to thermostat AUX outputs. (Used by all protocol software, but should not be used when aux is the primary heat source.)
420E | AuxHeaterHeatPumpLockoutEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled 1: enabled (Only used by S21 or P1P2. Unitary uses the common HP lockout enable stored in the "heatPumpLockoutTemp" variable.)
420F | AuxHeaterLockoutEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled 1: enabled (Used by all protocol software, but should not be used when aux is the primary heat source.)
4210 | AuxHeaterHeatPumpLockoutStatus | BIT | 0 | 1 | 0 | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: inactive 1: active; Used by protocol software to report when the HP is locked out.
4211 | AuxHeaterLockoutStatus | BIT | 0 | 1 | 0 | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: inactive 1: active; Used by the protocol software to report when the aux heat source is locked out. (Used by all protocol software (?).)
4212 | AuxHeaterLockoutHysteresis | UINT8 | 1 | 3 | 3 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Temperature band in °C before disable lockout once enabled. For aux heat lockout is degrees below, for HP lockout is degrees above. This is not an installer setting but could be in the future.
4213 | AuxHeaterTonToffEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: disabled 1: enabled; Only used by CT aux heat software; When off, the aux heat source is controlled by same logic as heater strip, and if both exist both are turned on and off at the same time.
4214 | P1P2S21AuxHeaterIndoorFanSpeed | UINT8 | 0 | 7 | 5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
4215 | P1P2S21AuxFanSettingMemoryWriteTimer | UINT8 | 0 | 120 | 20 | TRUE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | TRUE | TRUE | Time in minutes to enforce between writing fan speed and fan field settings to indoor unit, to prevent exceeding the 100k lifetime memory write limit on some units. This timer is for limiting automated writing of these settings when being used to control the fan for aux devices like heaters, humidifiers, and dehumidifiers.
// Aux device status
0x4220 | AuxHumidifierStatus | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: off; 1: on; Used by protocol software to report when this aux device is running to drive display of corresponding status message.
0x4221 | AuxDehumidifierStatus | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: off; 1: on; Used by protocol software to report when this aux device is running to drive display of corresponding status message.
0x4222 | AuxVentilatorStatus | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | NOT USED YET; 0: off; 1: on;
0x4223 | AuxHeaterStatus | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | 0: off; 1: on; Used by protocol software to report when this aux device is running to drive display of corresponding status message.
// New Fit control variables
0x4240 | ctZoneAirflowReduction | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; Allows CFM to go down to 40%. In the v2.3 release this variable is set to true automatically by the UI when an EWC zone board is added to a system.
0x4241 | ctCirculationSelection | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; default ON, turned off when EWC zoning system added, installer can turn ON again in UI. Added in v2.3 release.
0x4242 | ctOutdoorHeatBoostModeEnable | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: off; 2: on; default is Off since makes equipment less efficient. Selection driven by check box in settings in UI.
0x4243 | ctCFMrequirementsSupported | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not supported; 1: supported; From equipment to indicate if this feature is supported.
0x4244 | ctCFMrequirements | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED by UI; In %, MOM bus and datamap value are multiplied by 2, must divide by 2 before display. Not Saved in equipment. Intended to be used by zoning system to restrict airflow of indoor unit. May not be fully implemented in ODUs.
0x4245 | ctCFMrequirementsEnable | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED by UI; 0: disabled; 1: enabled;
0x4246 | ctRatedPowerUpperLimitSupported | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not supported; 1: supported; From outdoor unit to indicate if this OpenADR feature is supported. Used by UI to display or not display this hidden feature after a long press on the "response settings" text in the "demand response" screen.
0x4247 | ctRatedPowerUpperLimit | UINT8 | 0 | 100 | 100 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In %, CT multiplies by 2 before sending across CT bus. Not Saved in equipment. UI only allows values of 0%, 40%, 70%, or 100% in v2.7 release where it is a hidden setting. Used in OpenADR implementation.
0x4248 | ctRatedPowerUpperLimitEnable | UINT8 | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: disabled; 1: enabled; From UI to equipment to communicate when to enable the "ctRatedPowerUpperLimit" setting. Used in OpenADR implementation.
0x4249 | ODPowerConsumptionDemandSupported | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: not supported; 1: supported; Indicates support for Power Consumption Demand by ODU software (0x01 fixed for R32 FIT); If supported, the 3 associated variables below will show up along with the Power Upper Limit settings, in the "response settings" after a long press on this text on the "demand response" screen.
0x424A | ODPowerConsumptionDemandSignal | UINT8 | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | ODPowerConsumptionDemand Signal 0 = OFF, 1 = ON;
0x424B | ODPowerConsumptionDemandTarget | UINT16 | 0 | 10000 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | ODPowerConsumptionDemandTarget 0 - 10000W (increment: 1W);
0x424C | ODPowerConsumptionDmdStatus | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: OFF; 1: ON; ODPower Consumption Demand Operating status;
// New Fit status data variables (gen 2 and 3)
0x4260 | ctOutdoorFrequencyInPercent | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (current frequency) / (highest frequency) * 200, so in 0.5% increments. Divide by 2 before display for 100% scale. Is percent of highest compressor speed that the unit is currently operating at. Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4261 | ctCoolingRatedPower | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Watts/10; multiply by 10 before display; Fixed value for each model; Only valid for DX9/DZ9 20 SEER and equivalent models, and only for rated combinations (though still reported).
0x4262 | ctHeatingRatedPower | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Watts/10; multiply by 10 before display; Fixed value for each model; Only valid for DX9/DZ9 20 SEER and equivalent models, and only for rated combinations (though still reported).
0x4263 | ctOutdoorPower | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Watts/10; multiply by 10 before display; calculated from current measured by outdoor unit. Data valid for Fit gen3, DX9/DZ9 20 SEER, and equivalent models.
0x4264 | ctIndoorPower | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Watts*10; divide by 10 before displaying; calculated from rotation speed of indoor motor; Data valid for Fit gen3, DX9/DZ9 20 SEER, and equivalent models.
0x4265 | ctIndoorRatedCFM | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In CFM/10; multiply by 10 before display; Fixed value for each model; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4266 | ctOutdoorOperationMode | UINT8 | 0 | 0x1F, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0:Stop; 1:Preparation_for_Reboot; 2:Pre_Cooling; 3:Pre_Heating; 4:Cooling_Startup; 5:Cooling; 6:Cooling_Oilreturn; 7:Cooling_Pump_Down; 8:Heating_Startup; 9:Heating; 10:Heating_Oilreturn; 11:Defrost; 12:Heating_Pump_Down; 15:Pre_Defrost; 16:After_Defrost; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4267 | ctCurrentCompressorRPS | UINT16 | 0 | 2000,0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Current compressor RPS. 0=stopped; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4268 | ctCompressorCurrent | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | In Amps*10 or 0.1A steps; Divide by 10 before display; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4269 | ctRetryCode | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Display as decimal value; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426A | ctInverterCurrent | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0.0A to 51.0A in 0.2A steps; Divide by 5 before displaying; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426B | ctInverterFinTemp | FLOAT | -40 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Range of -30°C to 225°C in 1°C steps; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426C | ctTargetCompressorspeed | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Compressor RPS in 1.0 RPS steps, 00 when stopped. Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426D | ctOperationRequestToCompressor | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426E | ctReversingValve | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x426F | ctOperationRequestToODFanMotor | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4270 | ctODFanMotorCurrent | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0.0A to 3.1A in 0.1A steps; Divide by 10 before displaying; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4271 | ctTargetODFanRPM | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 RPM to 2550 RPM in 10 RPM steps; multiply by 10 before displaying; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4272 | ctOutdoorEEVOpening | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | [(Target opening)/(Maximum opening or 480 pulses)] * 100; 0% to 100% in 1% steps. Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4273 | ctIDCoilFreezeProtection | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4274 | ctCrankCaseHeaterOnOff | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4275 | ctDrainPanHeaterOnOff | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2 and gen3 and equivalent models, NOT for DX9/DZ9 20 SEER and equivalent models that don't have a drain pan heater.
0x4276 | ctPreHeatOnOff | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Off; 1: On; 0xFF: not supported; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4277 | ctPreHeatOutput | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0W to 124 W in 4@ increments; Multiply by 4 before displaying; Data valid for Fit gen2, gen3, and DX9/DZ9 20 SEER and equivalent models.
0x4278 | ct4WayValveFixActive | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: inactive; 1: active; Not shown in UI, but used for troubleshooting. Shows when the CT PIC24 4-way valve fix algorithm is active and preventing cool calls until the ODU resets (as included in v3.3.11 software).
// CT AHU and EEV Coil Status Data for R32
0x4280 | ctAHFanMotorRPM | UINT16 | 0 | 16384, 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Fan Moter Speed in RPM, divide by 4 to display (in 0.25 rpm steps); Hidden in UI;
0x4281 | ctAHEEVOpenRate | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | EEV Open rate in %, divide by 2 to display (in 0.5% steps); Hidden in UI;
0x4282 | ctAHHeatingStage | UINT8 | 0 | 7, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: No Heater Control; 1: Reserved (as 1 Stage); 2: 2 Stage Control; 3: 3 Stage Control; else: Reserved; same data as new 'ctAHHeatingStageGG' variable, only this source is the old CTUM mesage;
0x4283 | ctAHRefrigerantTypeNew | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: R410A; 1: R32; 2-254: Reserved; 255:Not available; this is a new generic data variable, and when populated replaces the old 'ctAHRefrigerantType' CHAR type variable in the UI.
0x4284 | ctAHR32GasLeakStatus | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Normal; 1: Mitigation for Gas Leak detection active; generated with A0 critical error.
0x4285 | ctAHHeatingStageGG | UINT8 | 0 | 7, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: No Heater Control; 1: Reserved (as 1 Stage); 2: 2 Stage Control; 3: 3 Stage Control; else: Reserved; same data as 'ctAHHeatingStage' variable, only from new GET GENERIC CT message;
0x4286 | ctAHAuxAlarmStatus | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 = OFF; 1 = ON; reports current state of aux alarm;
0x4287 | ctEEVCoilEEVOpenRate | UINT8 | 0 | 200, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | EEV Open rate in %, divide by 2 to display (in 0.5% steps); Hidden in UI;
// CT R32 IDU gas leak variables
0x4290 | ctIndoorR32GasLeakDetectEnable | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: OFF; 2: ON (Default); for turning R32 leak safety system ON or OFF;
0x4291 | ctIndoorR32LeakSignalReset | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; (removed from R32 IDU release); 0: OFF; 1: ON; for resetting the leak signal;
0x4292 | ctIndoorR32LeakResetTime | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; (removed from R32 IDU release); 0 : 10m (Default); 1 : 15m; 2 : 20m; 3 : 5 min.; reset time for the refrigerant leak error (in minutes)
0x4293 | ctIndoorR32LeakFixTime | UINT8 | 0 | 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | NOT USED; (removed from R32 IDU release); 0 : 10m (Default); 1 : 15m; 2 : 20m; 3 : 5m; Confirmation time for a refrigerant leak error;
0x4294 | ctIndoorR32LeakAirflow | UINT8 | 0 | 4, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1 : LL; 2 : L (Default); 3 : M; 4 : H; Fan speed (tap) during refrigerant leak mitigation;
0x4295 | ctIndoorR32LeakOprTest | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: OFF (Default); 2: ON; for turning on the R32 leak detection test.
0x4296 | ctIndoorR32GasLeakSamples | UINT8 | 0 | 3, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: L; 2: M (Default); 3: H ; Gas Leak Sampling Data. Choose the quantities of sampling data used for determining the gas leak leve
// CT ODU Control and Status Data for R32 and ccHP
0x42A0 | ctOutdoorSubTypeIdentification | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 2= Enhanced Fit with ccHP features; 1=CCHP, 0 or 0xFF=Other; (3 to 254 : Reserve area for future use); '1' and '2' value used to freeze RPS offset values at default.
0x42A1 | ctOutdoorFan2Request | UINT8 | 0 | 1, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: OFF or no ODU fan2; 1: ON;
0x42A2 | ctOutdoorFan2Current | UINT8 | 0 | 31, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0.0 A to 3.1A, in 0.1 A increments (divide by 10 to display);
0x42A3 | ctOutdoorTargetFan2RPM | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 RPM to 2540 RPM, in 10 RPM increments (multiply by 10 to display); 255: invalid/unavailable;
0x42A4 | ctOutdoorFan2CurrentFrequency | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0 RPM to 2540 RPM, in 10 RPM increments (multiply by 10 to display); 255: invalid/unavailable;
0x42A5 | ctOutdoorLiquidinjectionEEVOpening | UINT8 | 0 | 0x7F, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Target Opening / Maximum Opening(480pls) * 100; 127 = invalid or no data so should display "--". 0% to 100%, in 1.0 % increments
0x42A6 | ctOutdoorHighPressure | INT16 | -16000 | 16383, 0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Whole Part of Pressure (PSI)
0x42A7 | ctOutdoorRefrigerantType | UINT8 | 0 | 254, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: R410A; 1: R32; 0xFF: not available
0x42A8 | ODAvgSubCoolTempCorrected | INT16 | -1000 | 4000,0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Moving Average of SC' - (temp in °F)*10; (expected range : -58.0 F to 122.0F) Need to DIVIDE BY 10, and also SUBTRACT 32 BEFORE DISPLAY to correct error in ODU calculation.
0x42A9 | ODChargeModeState | UINT8 | 0 | 7, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Charge Mode State (for display under the new System Verification Test when enabled); 0: Do not display this setting or the "ODAvgSubCoolTempCorrected " value; Display the following text on thermostat based on its value: 1: "Outdoor Temp out of range - Please use gauges to adjust charge" 2: "System stabilizing" 3: "Outdoor fan speed not in range" 4: "Compressor speed not in range" 5: "Indoor SH not in range" 6: "SC in range (moving average)" 7: "In range - confirming continuous stability"
0x42AA | ODSystemTestState | UINT8 | 0 | 7, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | System Test state (for display under the new System Test); 0: "System test required" 1: "Initial test successful"
0x42AB | ctPowerfulHeatingEnable | UINT8 | 1 | 2, 0xFF | 0xFF | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 1: Powerful heating off; 2: Powerful heating on; When HP heat demand is < 50% (or <25% for 2, 3 ton ccHP, <45% for 5-ton enhanced FIT) and this feature is enabled, it increases the minimum heat demand the ODU operates at to give better heating performance.
0x42AC | ctPowerfulHeatingStatus | UINT8 | 0 | 7, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | 0: Powerful heating not active; 1: Powerful heating active;
0x42AD | ctIndoorSHMovingAvg | INT16 | -1000 | 4000, 0x7FFF | 0x7FFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | (temp in °F)*10; reported by ODU (where calculation is done); Need to DIVIDE BY 10, and also SUBTRACT 32 BEFORE DISPLAY to correct error in ODU calculation.
0x42AE | ctODCompressorDCVoltage | UINT16 | 0 | 511, 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | Outdoor unit compressor DC voltage; added to Fit Gen3 and ccHP in ~Feb. 2024 production. Population of this variable may be used to trigger display of the '0s' option for the OD heat and cool airflow delays.
//VRV and Mini-split System Information and settings
0x5000 | P1P2S21equipmentStatus | UINT8 | 1 | 2 | 1 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 1: cool; 2: heat; (Reports current P1P2/S21 master mode, which is the allowed operation modes for the follower. Therm on/off has no impact on this. If off, it is the last used mode);
0x5001 | P1P2S21CoolingCapability | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: None; 1: cooling capable
0x5002 | P1P2S21HeatingCapability | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: None; 1: heating capable
0x5003 | S21ModeChangeRefusal | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0=OFF; 1=ON
0x5010 | P1P2S21HumModeEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used by P1P2/S21 software to tell when humidifying is active; for use by Aux Control software and dealer services.
0x5011 | P1P2S21DehumModeEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used by P1P2/S21 software to tell when dehumidifying is active; for use by Aux Control software and dealer services.
0x5012 | S21SyncWithIndoorTemp | BIT | 0 | 1 | 1 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Disable (floor mount unit); 1: Enable (non-floor mount unit)
0x5013 | P1P2S21AutoChangeoverStartTimerDiff | FLOAT | 0.5 | 2 | 0.5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0.5 to 2.0°C in 0.5°C degree steps; Auto changeover start timer differential
0x5014 | P1P2S21ForcedAutoChangeoverDiff | FLOAT | 0.5 | 2 | 0.5 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0.5 to 2.0°C in 0.5°C degree steps; Forced Auto changeover differential (from start timer differential).
0x5015 | P1P2S21HeatCoolChangeoverTimer | UINT8 | 15 | 60 | 15 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 15, 30, 45, and 60 minutes; Guard timer for changeover, started from the previous change of mode.
0x5016 | S21ComfortModeExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: none; 1: comfort mode exists
0x5017 | S21ComfortModeEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: off; 1: enabled;
0x5018 | P1P2MaxCoolSetpoint | FLOAT | 10 | 32.2 | 32.2 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | NOT USED; P1P2 CSP upper limit from equipment in Celsius
0x5019 | P1P2MinCoolSetpoint | FLOAT | 10 | 32.2 | 10 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | NOT USED; P1P2 CSP lower limit from equipment in Celsius
0x501A | P1P2MaxHeatSetpoint | FLOAT | 10 | 32.2 | 32.2 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | NOT USED; P1P2 HSP upper limit from equipment in Celsius
0x501B | P1P2MinHeatSetpoint | FLOAT | 10 | 32.2 | 10 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | NOT USED; P1P2 HSP lower limit from equipment in Celsius
0x501C | S21HeatModeMinTimeForDefrost | UINT8 | 0 | 255 | 240 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | The time in minutes required to run heat continuously to guarantee that defrost has a chance to run. Used by the S21 fan control algorithm to ensure defrost can run often enough.
0x501D | S21MaxTimeBetweenDefrost | UINT8 | 0 | 255 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | The maximum time in minutes between longer heat runs (as defined by the 'S21HeatModeMinTimeForDefrost' variable) to ensure defrost can run often enough . Used by the S21 fan control algorithm to ensure defrost can run often enough.
0x501E | S21HeatModeMinTimeForDefrost2 | UINT8 | 0 | 255 | 240 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | The time in minutes required to run heat continuously to guarantee that defrost has a chance to run. Used by the S21 fan control algorithm to ensure defrost can run often enough. Replaces previous "S21HeatModeMinTimeForDefrost" variable to force change of default time.
0x501F | S21MaxTimeBetweenDefrost2 | UINT8 | 0 | 255 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | The maximum time in minutes between longer heat runs (as defined by the 'S21HeatModeMinTimeForDefrost' variable) to ensure defrost can run often enough . Used by the S21 fan control algorithm to ensure defrost can run often enough. Replaced previous "S21MaxTimeBetweenDefrost2" variable to force new default time.
//VRV and Mini-split Fan information and settings
0x5020 | P1P2S21FanControlExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: no fan; 1: Fan; Used by IDU to report if fan control is supported.
0x5021 | P1P2S21NumFanSpeeds | UINT8 | 0 | 5 | 3 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 3: 3 steps; 5: 5 steps; Used by IDU to report the number of fan speeds supported. 3 means L, M. and H are supported, 5 means L, ML, M, MH, and H are supported.
0x5022 | P1P2S21NumFanSpeedsCooling | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
0x5023 | P1P2S21NumFanSpeedsHeating | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Auto 1: Low 2: Low-Medium 3: Medium 4: Medium-High 5-7: High; This is the fan speed selected in the UI by the user. Speeds displayed for selection in the UI depend on the IDU capabilities reported in the "P1P2S21NumFanSpeeds" variable.
0x5024 | P1P2FanSpeedAutoControlExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: none; 1: fan auto control exists; Used by IDU to report if auto fan speed is supported.
0x5025 | P1P2S21FanUpDownExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: no up/down control; 1: up/down control exists; Used by IDU to report if vertical louver control is supported.
0x5026 | P1P2FanUpDownAutoControlExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: none; 1: fan up/down auto control exists; Used by IDU to report if auto setting for vertical louver control is supported.
0x5027 | P1P2S21FanCoolDirection1 | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Position 0; 1: Position 1; 2: Position 2; 3: Position 3; 4: Position 4; 5: N/A; 6: STOP; 7: Swing(Oscillation); Used by UI to report selected vertical louver position for cooling mode.
0x5028 | P1P2S21FanCoolDirectionAuto1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Set direction; 1: auto; Used by UI to report if auto vertical louver control for cooling is selected. If auto is selected, the "P1P2S21FanCoolDirection1" variable is ignored.
0x5029 | P1P2S21FanHeatDirection1 | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Position 0 1: Position 1 2: Position 2 3: Position 3 4: Position 4 5: N/A 6: STOP 7: Swing(Oscillation)
0x502A | P1P2S21FanHeatDirectionAuto1 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Set direction; 1: auto;
0x502B | P1P2S21FanLeftRightExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: no left/right control; 1: left/right control exists
0x502C | P1P2FanLeftRightAutoControlExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: none; 1: fan left/right auto control exists
0x502D | P1P2S21FanCoolDirection2 | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Position 0 1: Position 1 2: Position 2 3: Position 3 4: Position 4 5: N/A 6: STOP 7: Swing(Oscillation)
0x502E | P1P2S21FanCoolDirectionAuto2 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Set direction; 1: auto;
0x502F | P1P2S21FanHeatDirection2 | UINT8 | 0 | 7 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Position 0 1: Position 1 2: Position 2 3: Position 3 4: Position 4 5: N/A 6: STOP 7: Swing(Oscillation)
0x5030 | P1P2S21FanHeatDirectionAuto2 | BIT | 0 | 1 | 0 | TRUE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Set direction; 1: auto;
0x5031 | P1P2UnitType | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2 Unit 0);
0x5032 | S21IndoorUnitType | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR S21);
//VRV and Mini-split Equipment Errors
0x5040 | P1P2S21ErrorLevel | UINT8 | 0 | 8 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | bit0: critical; bit1: major; bit3: minor
0x5041 | P1P2S21ErrorCode | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | Hex error code
0x5042 | P1P2S21DetailedErrorCode | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | Hex detailed error code.
0x5043 | P1P2S21ClearErrorFlag | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: OFF; 1: ON; After clearing errors using system mode, PIC24 software uses to ask UI to remove the request to clear errors.
0x5044 | P1P2S21ClearErrorFlagChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: OFF; 1: ON; UI Uses to request clearing of Error by turning system mode OFF, then ON again.
0x5045 | P1P2ErrorCodeUnitNumber | UINT8 | 0 | 15 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | FALSE | TRUE | TRUE | 0-15: Unit Number
//S21 Status data (mini-split)
0x5050 | S21IndoorTempValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5051 | S21IndoorSuctionTemp | INT16 | -1000 | 2000 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Indoor suction temperature in Celsius
0x5052 | S21OutdoorAirTempValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5053 | S21OutdoorAirTemp | INT16 | -1000 | 2000 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Outdoor air temperature in Celsius
0x5054 | S21SerialComVersion | UINT8 | 30 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0x30: Ver.0; 0x31: Ver.1; 0x32: Ver.2; 0x33: Ver.3; 0xFF: Version unknown
0x5055 | S21DischargePipeTemp | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Discharge Pipe temperature in Celsius; divide by 2 before display
0x5056 | S21OutdoorHeatExchangerTemp | INT16 | -1000 | 2000 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Outdoor heat exchanger temperature in Celsius; divide by 10 before display
0x5057 | S21ElectricCurrentFlow | FLOAT | 0.0 | 255.9 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Electric current
0x5058 | S21OutdoorFanRPM | UINT8 | 0 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Outdoor fan RMP; multiply by 10 before display
0x5059 | S21OutdoorLiquidPipeTemp | INT16 | -1000 | 2000 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Outdoor liquid pipe temperature in Celsius; divide by 10 before display;
0x505A | S21PowerConsumption | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | Power consumption
0x505B | S21EEVaperture | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | EEV open % (in pulses)
0x505C | S21IndoorUnitSerialNumber | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | ASCII
0x505D | S21IndoorUnitModelName | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | ASCII
0x505E | S21OutdoorUnitSerialNumber | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | ASCII
0x505F | S21OutdoorUnitModelName | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | ASCII
0x5060 | S21ThermOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: Cool or Heat therm OFF mode 1: Cool or Heat therm ON mode
0x5061 | S21DischargePipeTempValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5062 | S21OutdoorHeatExchangerTempValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5063 | S21ElectricCurrentFlowValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5064 | S21OutdoorFanRPMValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5065 | S21OutdoorLiquidPipeTempValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5066 | S21PowerConsumptionValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5067 | S21EEVapertureValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5070 | S21DemandSettingEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0: disable; 1: enable; (for future use)
0x5071 | S21DemandLevelSetting | UINT8 | 0 | 100 | 40 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | 0% to 100%; (for future use)
//P1P2 (VRV) Equipment Control
0x5100 | P1P2ForcedStop | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used to report a Forced Stop condition so the UI will be locked to prevent any changes.
0x5101 | P1P2ExternalStop | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used to report an External Stop condition so the UI will be locked to prevent any changes.
0x5102 | P1P2OutdoorUnitTestOperationActive | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used to report when test operation from the outdoor unit is active so the UI will be locked to prevent any changes.
0x5103 | P1P2ModeMasterFollowerClass | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Master (Type C); 1: Follower (Type A); 2: Neutral (Type D); (UI selection written here);
0x5104 | P1P2EquipmentModeMasterFollowerClass | UINT8 | 0 | 2, 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Master (Type C); 1: Follower (Type A); 2: Neutral (Type D); (equipment reported value);
//P1P2 (VRV) Field Settings
0x5200 | P1P2ReceivedFieldSettingSW0 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5201 | P1P2ReceivedFieldSettingSW1 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5202 | P1P2ReceivedFieldSettingSW2 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5203 | P1P2ReceivedFieldSettingSW3 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5204 | P1P2ReceivedFieldSettingSW4 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5205 | P1P2ReceivedFieldSettingSW5 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5206 | P1P2ReceivedFieldSettingSW6 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5207 | P1P2ReceivedFieldSettingSW7 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5208 | P1P2ReceivedFieldSettingSW8 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5209 | P1P2ReceivedFieldSettingSW9 | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520A | P1P2ReceivedFieldSettingSWa | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520B | P1P2ReceivedFieldSettingSWb | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520C | P1P2ReceivedFieldSettingSWc | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520D | P1P2ReceivedFieldSettingSWd | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520E | P1P2ReceivedFieldSettingSWe | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x520F | P1P2ReceivedFieldSettingSWf | UINT8 | 0 | 0xFF | 15 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3: set value; bit4-7: allowable range; 15=not set:
0x5210 | P1P2SentFieldSettingSW0 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5211 | P1P2SentFieldSettingSW1 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5212 | P1P2SentFieldSettingSW2 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5213 | P1P2SentFieldSettingSW3 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5214 | P1P2SentFieldSettingSW4 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5215 | P1P2SentFieldSettingSW5 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5216 | P1P2SentFieldSettingSW6 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5217 | P1P2SentFieldSettingSW7 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5218 | P1P2SentFieldSettingSW8 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5219 | P1P2SentFieldSettingSW9 | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521A | P1P2SentFieldSettingSWa | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521B | P1P2SentFieldSettingSWb | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521C | P1P2SentFieldSettingSWc | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521D | P1P2SentFieldSettingSWd | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521E | P1P2SentFieldSettingSWe | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x521F | P1P2SentFieldSettingSWf | UINT8 | 0 | 15 | 15 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value; 15=not set;
0x5220 | P1P2PopulatedUnits | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Each bit represents a unit; 0: no unit; 1: unit present
0x5221 | P1P2FieldSettingModeNumber | UINT8 | 0 | 25 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Modes 10 to 15 and Modes 20-25; 0 is default when no mode selected. A non-zero value initiates a request to read or write.
0x5222 | P1P2FieldSettingUnitNum | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: Unit Number
0x5223 | P1P2FieldSettingUnitNumChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Read (or OFF) 1: Write (or ON); used to Read from (using the values in the P1P2...ReceivedFieldSettingSW variables) or Write to (using the P1P2...SentFieldSettingSW variables) the field settings for the selected unit number; used for normal, non-public, and super secret field settings;
0x5224 | P1P2ResidentialSettings | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON
0x5225 | P1P2FieldSettingModeNumChangeRequest | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF (no new data) 1: ON (new data received); used by P1P2 software to report when new field setting data is available in the P1P2...ReceivedFieldSettingSW variables as a result of a read or write request; used for normal, non-public, and super secret field settings;
0x5226 | P1P2FieldSettingExitFlag | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | The UI sets to 1 (TRUE) when exiting the field setting menus if changes were made. The P1P2 software sets it back to 0 when it has restarted P1P2 communication to process the field setting changes.
0x5227 | P1P2LockFieldSettingsFlag | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: FALSE; 1: TRUE; If the UI checks and finds this variable is TRUE when starting a field setting operation, it delay the operation and after a timeout period generate an error message if the operation cannot start. If FALSE, the UI will set to TRUE before starting the field setting operation, then return to FALSE after completing the field setting operation.
//P1P2 (VRV) Non-public Field Settings
0x5230 | P1P2NonPublicReceivedFieldSettingSW0 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5231 | P1P2NonPublicReceivedFieldSettingSW1 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5232 | P1P2NonPublicReceivedFieldSettingSW2 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5233 | P1P2NonPublicReceivedFieldSettingSW3 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5234 | P1P2NonPublicReceivedFieldSettingSW4 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5235 | P1P2NonPublicReceivedFieldSettingSW5 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5236 | P1P2NonPublicReceivedFieldSettingSW6 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5237 | P1P2NonPublicReceivedFieldSettingSW7 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5238 | P1P2NonPublicReceivedFieldSettingSW8 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5239 | P1P2NonPublicReceivedFieldSettingSW9 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523A | P1P2NonPublicReceivedFieldSettingSWa | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523B | P1P2NonPublicReceivedFieldSettingSWb | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523C | P1P2NonPublicReceivedFieldSettingSWc | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523D | P1P2NonPublicReceivedFieldSettingSWd | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523E | P1P2NonPublicReceivedFieldSettingSWe | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x523F | P1P2NonPublicReceivedFieldSettingSWf | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5240 | P1P2NonPublicSentFieldSettingSW0 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5241 | P1P2NonPublicSentFieldSettingSW1 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5242 | P1P2NonPublicSentFieldSettingSW2 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5243 | P1P2NonPublicSentFieldSettingSW3 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5244 | P1P2NonPublicSentFieldSettingSW4 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5245 | P1P2NonPublicSentFieldSettingSW5 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5246 | P1P2NonPublicSentFieldSettingSW6 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5247 | P1P2NonPublicSentFieldSettingSW7 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5248 | P1P2NonPublicSentFieldSettingSW8 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5249 | P1P2NonPublicSentFieldSettingSW9 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524A | P1P2NonPublicSentFieldSettingSWa | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524B | P1P2NonPublicSentFieldSettingSWb | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524C | P1P2NonPublicSentFieldSettingSWc | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524D | P1P2NonPublicSentFieldSettingSWd | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524E | P1P2NonPublicSentFieldSettingSWe | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x524F | P1P2NonPublicSentFieldSettingSWf | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5250 | P1P2NonPublicFieldSettingModeNumber | UINT8 | 0 | 59 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Modes 50 to 59; 0 is default when no mode selected. A non-zero value initiates a request to read or write.
0x5251 | P1P2NonPublicFieldSettingModeNumChangeRequest | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF (no new data) 1: ON (new data received); used by P1P2 software to report when new field setting data is available in the P1P2NonPublicReceivedFieldSettingSW variables as a result of a read or write request;
//P1P2 (VRV) Super Secret Field Settings
0x5260 | P1P2SuperSecretReceivedFieldSettingSW0 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5261 | P1P2SuperSecretReceivedFieldSettingSW1 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5262 | P1P2SuperSecretReceivedFieldSettingSW2 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5263 | P1P2SuperSecretReceivedFieldSettingSW3 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5264 | P1P2SuperSecretReceivedFieldSettingSW4 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5265 | P1P2SuperSecretReceivedFieldSettingSW5 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5266 | P1P2SuperSecretReceivedFieldSettingSW6 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5267 | P1P2SuperSecretReceivedFieldSettingSW7 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5268 | P1P2SuperSecretReceivedFieldSettingSW8 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5269 | P1P2SuperSecretReceivedFieldSettingSW9 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526A | P1P2SuperSecretReceivedFieldSettingSWa | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526B | P1P2SuperSecretReceivedFieldSettingSWb | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526C | P1P2SuperSecretReceivedFieldSettingSWc | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526D | P1P2SuperSecretReceivedFieldSettingSWd | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526E | P1P2SuperSecretReceivedFieldSettingSWe | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x526F | P1P2SuperSecretReceivedFieldSettingSWf | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bits 1-3 is value (0-15); for bits 4-7, 0 means not supported, 15 means supported.
0x5270 | P1P2SuperSecretSentFieldSettingSW0 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5271 | P1P2SuperSecretSentFieldSettingSW1 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5272 | P1P2SuperSecretSentFieldSettingSW2 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5273 | P1P2SuperSecretSentFieldSettingSW3 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5274 | P1P2SuperSecretSentFieldSettingSW4 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5275 | P1P2SuperSecretSentFieldSettingSW5 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5276 | P1P2SuperSecretSentFieldSettingSW6 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5277 | P1P2SuperSecretSentFieldSettingSW7 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5278 | P1P2SuperSecretSentFieldSettingSW8 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5279 | P1P2SuperSecretSentFieldSettingSW9 | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527A | P1P2SuperSecretSentFieldSettingSWa | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527B | P1P2SuperSecretSentFieldSettingSWb | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527C | P1P2SuperSecretSentFieldSettingSWc | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527D | P1P2SuperSecretSentFieldSettingSWd | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527E | P1P2SuperSecretSentFieldSettingSWe | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x527F | P1P2SuperSecretSentFieldSettingSWf | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: set value
0x5280 | P1P2SuperSecretFieldSettingModeNumber | UINT8 | 0 | 65 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Modes 60-65; 0 is default when no mode selected. A non-zero value initiates a request to read or write.
0x5281 | P1P2SuperSecretFieldSettingModeNumChangeRequest | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF (no new data) 1: ON (new data received); used by P1P2 software to report when new field setting data is available in the P1P2SuperSecretReceivedFieldSettingSW variables as a result of a read or write request;
//P1P2 (VRV) Group Address Settings
0x5300 | P1P2GroupAddressExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: None; 1: Exists; If exists, UI displays group address menu.
0x5301 | P1P2GroupAddressEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF; 1: ON; Set to ON by P1P2 software when group address data is readyand is cleared by P1P2 at end of sequence after UI writes 0 to "P1P2GroupAddressSetting".
0x5302 | P1P2GroupAddressSetting | UINT8 | 0 | 10 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: received; 5: Read all 6: Write all 7: Delete all 8: Read individually 9: Write individually 10: Delete individually; Used by the UI to start a group address sequence between UI and P1P2 software, and at the end of the sequence is set to 0 by the UI to indicate all data received.
0x5303 | P1P2GroupAddressChangeRequestEnable | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: OFF 1: ON;
0x5304 | P1P2GroupAddressAllowableRange | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0: address 0-15; bit1: address 16-31; bit2: address 32-47; bit3: address 48-63; bit4: address 64-79; bit5: address 80-95; bit6: address 96-111; bit7: address 112-127; Tells the UI the allowable range of group addresses to be displayed for possible selection.
0x5305 | P1P2GroupAddressWrittenReceived | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address; 0xFF = none (deleted); Used to write an address selected for a unit from the UI to the P1P2 software (and on to the IDU);
0x5306 | P1P2GroupAddressWrittenSent | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address; 0xFF = none (deleted); Used to receive a group address for a unit from the P1P2 software (sent by the IDU);
0x5307 | P1P2GroupAddressUnitNumber | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: Unit Number; should be restricted by UI the existing units reported in the "P1P2PopulatedUnits" variable.
0x5308 | P1P2GroupAddressControl | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Complete 1: Processing; Used by P1P2 software to acknowledge UI request for group address, is cleared by the P1P2 software at end of a read, write, or delete sequence.
//P1P2 (VRV) Airnet Address Settings
0x5310 | P1P2IndoorUnitAirnetAddressExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: None; 1: Exists; If exists, UI displays indoor airnet addresses.
0x5311 | P1P2IndoorUnitAirnetAddressEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF; 1: ON; Set to ON by P1P2 software when indoor airnet address data is ready, cleared at end of sequence.
0x5312 | P1P2AirnetAddressSetting | UINT8 | 0 | 16 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: received; 11: Read indoor unit Airnet address; 12: Write indoor unit Airnet address; 13: Delete indoor unit Airnet address; 14: Read outdoor unit airnet address; 15: Write outdoor unit airnet address; 16: Delete outdoor unit airnet address; Used to start indoor or outdoor airnet address sequence between UI and P1P2 software;
0x5313 | P1P2AirnetAddressChangeRequestEnable | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: OFF 1: ON;
0x5314 | P1P2AirnetAddressIndoorUnitReceived | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address
0x5315 | P1P2AirnetAddressIndoorUnitSent | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address
0x5316 | P1P2OutdoorUnitAirnetAddressExists | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: None; 1: Exists; If exists, UI displays outdoor airnet address.
0x5317 | P1P2OutdoorUnitAirnetAddressEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF; 1: ON; Set to ON by P1P2 software when outdoor airnet address data is ready, cleared at end of sequence.
0x5318 | P1P2AirnetAddressOutdoorUnitReceived | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address
0x5319 | P1P2AirnetAddressOutdoorUnitSent | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255: Set address
0x531A | P1P2AirnetAddressUnitNumber | UINT8 | 0 | 15 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: Unit Number
0x531B | P1P2AirnetAddressUnitNumChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: OFF 1: ON;
0x531C | P1P2ODUAirnetAddressControl | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Complete 1: Processing; Used by P1P2 software to acknowledge UI request for outdoor airnet address, cleared at end of sequence.
0x531D | P1P2IDUAirnetAddressControl | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: Complete 1: Processing; Used by P1P2 software to acknowledge UI request for indoor airnet address, cleared at end of sequence.
//P1P2 (VRV) Draft Prevention Settings
0x5330 | P1P2DraftPreventionPresent | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: not present 1: present
0x5331 | P1P2DraftPreventionEnable | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; NOT USED
0x5332 | P1P2DraftPreventionChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON
//P1P2 (VRV) Forced Fan Settings
0x5340 | P1P2ForcedFanOnUnitNumber | UINT8 | 0 | 0xFF | 16 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-15: Unit number for forced fan ON; 16+: disable forced fan ON
0x5341 | P1P2ForcedFanOnChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON; Used by the UI to turn on the Fan for the unit specified by P1P2ForcedFanOnUnitNumber;
0x5342 | P1P2TestOperationEnable | BIT | 0 | 1 | 0 | FALSE | READWRITE | READWRITE | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: OFF 1: ON; not implemented in P1P2 PIC24 software.
0x5343 | P1P2TestOperationChangeRequest | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: OFF 1: ON;implemented in P1P2 PIC24 software, but not in UI so not tested as of v3.1 release.
//P1P2 (VRV) Outdoor Unit Status data
0x5400 | P1P2OutdoorUnitDataValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5401 | P1P2OutdoorUnitModelName | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII
0x5402 | P1P2OutdoorUnitSerialNumber | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI
0x5403 | P1P2OutdoorUnitFanTap | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0-255 (OPCA4 D[1])
0x5404 | P1P2CompressorPowerSupplyFrequency | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Compressor Power supply frequency in Hz
0x5405 | P1P2OutdoorUnitEEVOpenPulses | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | EEV open % (in pulses)
0x5406 | P1P2SolenoidValveOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCA4 D[0])
0x5407 | P1P2OutdoorAirThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Outdoor air thermistor temperature in Celsius
0x5408 | P1P2OutdoorUnitHeatExchangerThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Heat exchanger thermistor temperature in Celsius
0x5409 | P1P2OutdoorUnitDischargePipeThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU discharge pipe thermistor temperature in Celsius
0x540A | P1P2OutdoorUnitHeatExchangerDeicerThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Heat exchanger de-icer thermistor temperature in Celsius
0x540B | P1P2OutdoorUnitHeatExchangerGasPipeThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Heat exchanger gas pipe thermistor temperature in Celsius
0x540C | P1P2OutdoorUnitLiquidPipeThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Liquid Pipe Thermistor temperature in Celsius
0x540D | P1P2OutdoorUnitOperatingTime | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU operating time; multiply by 2 before displaying value
0x540E | P1P2OutdoorUnitFan1OperationTime | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Fan #1 operation time; multiply by 2 before displaying value
0x540F | P1P2OutdoorUnitFan2OperationTime | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Fan #2 operation time; multiply by 2 before displaying value
0x5410 | P1P2OutdoorUnitCompressor1OperationTime | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Compressor 1 operation time; multiply by 2 before displaying value
0x5411 | P1P2OutdoorUnitCompressor2OperationTime | UINT16 | 0 | 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ODU Compressor 1 operation time; multiply by 2 before displaying value
0x5412 | P1P2OutdoorUnitAddress | UINT8 | 0 | 0xFF | 0xFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Outdoor Unit D3 address
0x5413 | P1P2OutdoorUnitModelNameManual | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII
0x5414 | P1P2OutdoorUnitSerialNumberEquip | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU
0x5415 | P1P2OutdoorUnitSerialNumberEquipValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5416 | P1P2OutdoorUnitModelNameValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5417 | P1P2OutdoorUnitFanTapValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5418 | P1P2CompressorPowerSupplyFrequencyValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5419 | P1P2OutdoorUnitEEVOpenPulsesValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541A | P1P2SolenoidValveOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541B | P1P2OutdoorAirThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541C | P1P2OutdoorUnitHeatExchangerThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541D | P1P2OutdoorUnitDischargePipeThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541E | P1P2OutdoorUnitHeatExchangerDeicerThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x541F | P1P2OutdoorUnitHeatExchangerGasPipeThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5420 | P1P2OutdoorUnitLiquidPipeThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5421 | P1P2OutdoorUnitOperatingTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5422 | P1P2OutdoorUnitFan1OperationTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5423 | P1P2OutdoorUnitFan2OperationTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5424 | P1P2OutdoorUnitCompressor1OperationTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5425 | P1P2OutdoorUnitCompressor2OperationTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5426 | P1P2OutdoorUnitAddressValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//P1P2 (VRV) Indoor Unit Status data
0x5430 | P1P2IndoorUnitDataValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5431 | P1P2IndoorUnitModelName | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII
0x5432 | P1P2IndoorUnitSerialNumber | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI
0x5433 | P1P2IndoorUnitFanTap | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5434 | P1P2IndoorUnitFlapSwing | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5435 | P1P2IndoorUnitFanSpeed | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3]); multiply by 10 before displaying;
0x5436 | P1P2IndoorUnitEEVOpenPulses | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5437 | P1P2DrainPumpOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5438 | P1P2ElectricHeaterOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5439 | P1P2HumidifierOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x543A | P1P2AntiFreezeControlOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x543B | P1P2FloatOnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x543C | P1P2T1T2OnOff | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x543D | P1P2IndoorSuctionAirThermistor | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x543E | P1P2IndoorUnitHeatExchangerThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x543F | P1P2IndoorUnitHeatExchangerGasPipeThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5440 | P1P2IndoorUnitDischargeAirThermistor | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5441 | P1P2IndoorUnitOperatingTime | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time; multiply by 2 before displaying;
0x5442 | P1P2IndoorUnitFanOperationTime | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time; multiply by 2 before displaying;
0x5443 | P1P2IndoorUnitEnergizedTime | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time; multiply by 2 before displaying;
0x5444 | P1P2IndoorUnitAddress | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5445 | P1P2IndoorUnitModelNameManual | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII
0x5446 | P1P2IndoorUnitSerialNumberEquip | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU
0x5447 | P1P2IndoorUnitSerialNumberEquipValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5448 | P1P2IndoorUnitModelNameValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5449 | P1P2IndoorUnitFanTapValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544A | P1P2IndoorUnitFlapSwingValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544B | P1P2IndoorUnitFanSpeedValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544C | P1P2IndoorUnitEEVOpenPulsesValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544D | P1P2DrainPumpOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544E | P1P2ElectricHeaterOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x544F | P1P2HumidifierOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5450 | P1P2AntiFreezeControlOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5451 | P1P2FloatOnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5452 | P1P2T1T2OnOffValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5453 | P1P2IndoorSuctionAirThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5454 | P1P2IndoorUnitHeatExchangerThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5455 | P1P2IndoorUnitHeatExchangerGasPipeThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5456 | P1P2IndoorUnitDischargeAirThermistorValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5457 | P1P2IndoorUnitOperatingTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5458 | P1P2IndoorUnitFanOperationTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5459 | P1P2IndoorUnitEnergizedTimeValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x545A | P1P2IndoorUnitAddressValid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//P1P2 (VRV) additional system status data
0x5460 | P1P2ThermOnOffInformation | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | OPC10 D14 bit5
0x5470 | P1P2UIinputProhibitFlag | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 1 = UI input allowed; 2 = UI input prohibited
0x5500 | P1P2cspFromEquipment | FLOAT | 10 | 32.2, 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | CSP from ITM (for commercial software version)
0x5501 | P1P2hspFromEquipment | FLOAT | 10 | 32.2, 0xFFFF | 0xFFFF | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | HSP from ITM (for commercial software version)
//P1P2 (VRV) Indoor Unit #1 Status data
0x5600 | P1P2IndoorUnitDataValidUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5601 | P1P2IndoorUnitModelNameUnit1 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5602 | P1P2IndoorUnitSerialNumberUnit1 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5603 | P1P2IndoorUnitFanTapUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5604 | P1P2IndoorUnitFlapSwingUnit1 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5605 | P1P2IndoorUnitFanSpeedUnit1 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5606 | P1P2IndoorUnitEEVOpenPulsesUnit1 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5607 | P1P2DrainPumpOnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5608 | P1P2ElectricHeaterOnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5609 | P1P2HumidifierOnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x560A | P1P2AntiFreezeControlOnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x560B | P1P2FloatOnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x560C | P1P2T1T2OnOffUnit1 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x560D | P1P2IndoorSuctionAirThermistorUnit1 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x560E | P1P2IndoorUnitHeatExchangerThermistorUnit1 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x560F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit1 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5610 | P1P2IndoorUnitDischargeAirThermistorUnit1 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5611 | P1P2IndoorUnitOperatingTimeUnit1 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5612 | P1P2IndoorUnitFanOperationTimeUnit1 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5613 | P1P2IndoorUnitEnergizedTimeUnit1 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5614 | P1P2IndoorUnitAddressUnit1 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5615 | P1P2IndoorUnitModelNameManualUnit1 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5616 | P1P2IndoorUnitTypeUnit1 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5617 | P1P2IndoorUnitSerialNumberEquipUnit1 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #2 Status data
0x5620 | P1P2IndoorUnitDataValidUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5621 | P1P2IndoorUnitModelNameUnit2 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5622 | P1P2IndoorUnitSerialNumberUnit2 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5623 | P1P2IndoorUnitFanTapUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5624 | P1P2IndoorUnitFlapSwingUnit2 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5625 | P1P2IndoorUnitFanSpeedUnit2 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5626 | P1P2IndoorUnitEEVOpenPulsesUnit2 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5627 | P1P2DrainPumpOnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5628 | P1P2ElectricHeaterOnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5629 | P1P2HumidifierOnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x562A | P1P2AntiFreezeControlOnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x562B | P1P2FloatOnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x562C | P1P2T1T2OnOffUnit2 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x562D | P1P2IndoorSuctionAirThermistorUnit2 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x562E | P1P2IndoorUnitHeatExchangerThermistorUnit2 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x562F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit2 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5630 | P1P2IndoorUnitDischargeAirThermistorUnit2 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5631 | P1P2IndoorUnitOperatingTimeUnit2 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5632 | P1P2IndoorUnitFanOperationTimeUnit2 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5633 | P1P2IndoorUnitEnergizedTimeUnit2 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5634 | P1P2IndoorUnitAddressUnit2 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5635 | P1P2IndoorUnitModelNameManualUnit2 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5636 | P1P2IndoorUnitTypeUnit2 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5637 | P1P2IndoorUnitSerialNumberEquipUnit2 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #3 Status data
0x5640 | P1P2IndoorUnitDataValidUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5641 | P1P2IndoorUnitModelNameUnit3 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5642 | P1P2IndoorUnitSerialNumberUnit3 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5643 | P1P2IndoorUnitFanTapUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5644 | P1P2IndoorUnitFlapSwingUnit3 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5645 | P1P2IndoorUnitFanSpeedUnit3 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5646 | P1P2IndoorUnitEEVOpenPulsesUnit3 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5647 | P1P2DrainPumpOnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5648 | P1P2ElectricHeaterOnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5649 | P1P2HumidifierOnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x564A | P1P2AntiFreezeControlOnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x564B | P1P2FloatOnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x564C | P1P2T1T2OnOffUnit3 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x564D | P1P2IndoorSuctionAirThermistorUnit3 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x564E | P1P2IndoorUnitHeatExchangerThermistorUnit3 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x564F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit3 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5650 | P1P2IndoorUnitDischargeAirThermistorUnit3 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5651 | P1P2IndoorUnitOperatingTimeUnit3 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5652 | P1P2IndoorUnitFanOperationTimeUnit3 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5653 | P1P2IndoorUnitEnergizedTimeUnit3 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5654 | P1P2IndoorUnitAddressUnit3 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5655 | P1P2IndoorUnitModelNameManualUnit3 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5656 | P1P2IndoorUnitTypeUnit3 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5657 | P1P2IndoorUnitSerialNumberEquipUnit3 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #4 Status data
0x5660 | P1P2IndoorUnitDataValidUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5661 | P1P2IndoorUnitModelNameUnit4 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5662 | P1P2IndoorUnitSerialNumberUnit4 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5663 | P1P2IndoorUnitFanTapUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5664 | P1P2IndoorUnitFlapSwingUnit4 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5665 | P1P2IndoorUnitFanSpeedUnit4 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5666 | P1P2IndoorUnitEEVOpenPulsesUnit4 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5667 | P1P2DrainPumpOnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5668 | P1P2ElectricHeaterOnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5669 | P1P2HumidifierOnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x566A | P1P2AntiFreezeControlOnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x566B | P1P2FloatOnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x566C | P1P2T1T2OnOffUnit4 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x566D | P1P2IndoorSuctionAirThermistorUnit4 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x566E | P1P2IndoorUnitHeatExchangerThermistorUnit4 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x566F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit4 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5670 | P1P2IndoorUnitDischargeAirThermistorUnit4 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5671 | P1P2IndoorUnitOperatingTimeUnit4 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5672 | P1P2IndoorUnitFanOperationTimeUnit4 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5673 | P1P2IndoorUnitEnergizedTimeUnit4 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5674 | P1P2IndoorUnitAddressUnit4 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5675 | P1P2IndoorUnitModelNameManualUnit4 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5676 | P1P2IndoorUnitTypeUnit4 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5677 | P1P2IndoorUnitSerialNumberEquipUnit4 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #5 Status data
0x5680 | P1P2IndoorUnitDataValidUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5681 | P1P2IndoorUnitModelNameUnit5 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5682 | P1P2IndoorUnitSerialNumberUnit5 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5683 | P1P2IndoorUnitFanTapUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5684 | P1P2IndoorUnitFlapSwingUnit5 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5685 | P1P2IndoorUnitFanSpeedUnit5 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5686 | P1P2IndoorUnitEEVOpenPulsesUnit5 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5687 | P1P2DrainPumpOnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5688 | P1P2ElectricHeaterOnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5689 | P1P2HumidifierOnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x568A | P1P2AntiFreezeControlOnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x568B | P1P2FloatOnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x568C | P1P2T1T2OnOffUnit5 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x568D | P1P2IndoorSuctionAirThermistorUnit5 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x568E | P1P2IndoorUnitHeatExchangerThermistorUnit5 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x568F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit5 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5690 | P1P2IndoorUnitDischargeAirThermistorUnit5 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5691 | P1P2IndoorUnitOperatingTimeUnit5 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5692 | P1P2IndoorUnitFanOperationTimeUnit5 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5693 | P1P2IndoorUnitEnergizedTimeUnit5 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5694 | P1P2IndoorUnitAddressUnit5 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5695 | P1P2IndoorUnitModelNameManualUnit5 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5696 | P1P2IndoorUnitTypeUnit5 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5697 | P1P2IndoorUnitSerialNumberEquipUnit5 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #6 Status data
0x56A0 | P1P2IndoorUnitDataValidUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x56A1 | P1P2IndoorUnitModelNameUnit6 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x56A2 | P1P2IndoorUnitSerialNumberUnit6 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x56A3 | P1P2IndoorUnitFanTapUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x56A4 | P1P2IndoorUnitFlapSwingUnit6 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x56A5 | P1P2IndoorUnitFanSpeedUnit6 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x56A6 | P1P2IndoorUnitEEVOpenPulsesUnit6 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x56A7 | P1P2DrainPumpOnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x56A8 | P1P2ElectricHeaterOnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x56A9 | P1P2HumidifierOnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x56AA | P1P2AntiFreezeControlOnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x56AB | P1P2FloatOnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x56AC | P1P2T1T2OnOffUnit6 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x56AD | P1P2IndoorSuctionAirThermistorUnit6 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x56AE | P1P2IndoorUnitHeatExchangerThermistorUnit6 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x56AF | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit6 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x56B0 | P1P2IndoorUnitDischargeAirThermistorUnit6 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x56B1 | P1P2IndoorUnitOperatingTimeUnit6 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x56B2 | P1P2IndoorUnitFanOperationTimeUnit6 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x56B3 | P1P2IndoorUnitEnergizedTimeUnit6 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x56B4 | P1P2IndoorUnitAddressUnit6 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x56B5 | P1P2IndoorUnitModelNameManualUnit6 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x56B6 | P1P2IndoorUnitTypeUnit6 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x56B7 | P1P2IndoorUnitSerialNumberEquipUnit6 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #7 Status data
0x56C0 | P1P2IndoorUnitDataValidUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x56C1 | P1P2IndoorUnitModelNameUnit7 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x56C2 | P1P2IndoorUnitSerialNumberUnit7 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x56C3 | P1P2IndoorUnitFanTapUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x56C4 | P1P2IndoorUnitFlapSwingUnit7 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x56C5 | P1P2IndoorUnitFanSpeedUnit7 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x56C6 | P1P2IndoorUnitEEVOpenPulsesUnit7 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x56C7 | P1P2DrainPumpOnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x56C8 | P1P2ElectricHeaterOnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x56C9 | P1P2HumidifierOnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x56CA | P1P2AntiFreezeControlOnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x56CB | P1P2FloatOnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x56CC | P1P2T1T2OnOffUnit7 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x56CD | P1P2IndoorSuctionAirThermistorUnit7 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x56CE | P1P2IndoorUnitHeatExchangerThermistorUnit7 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x56CF | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit7 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x56D0 | P1P2IndoorUnitDischargeAirThermistorUnit7 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x56D1 | P1P2IndoorUnitOperatingTimeUnit7 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x56D2 | P1P2IndoorUnitFanOperationTimeUnit7 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x56D3 | P1P2IndoorUnitEnergizedTimeUnit7 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x56D4 | P1P2IndoorUnitAddressUnit7 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x56D5 | P1P2IndoorUnitModelNameManualUnit7 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x56D6 | P1P2IndoorUnitTypeUnit7 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x56D7 | P1P2IndoorUnitSerialNumberEquipUnit7 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #8 Status data
0x56E0 | P1P2IndoorUnitDataValidUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x56E1 | P1P2IndoorUnitModelNameUnit8 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x56E2 | P1P2IndoorUnitSerialNumberUnit8 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x56E3 | P1P2IndoorUnitFanTapUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x56E4 | P1P2IndoorUnitFlapSwingUnit8 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x56E5 | P1P2IndoorUnitFanSpeedUnit8 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x56E6 | P1P2IndoorUnitEEVOpenPulsesUnit8 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x56E7 | P1P2DrainPumpOnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x56E8 | P1P2ElectricHeaterOnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x56E9 | P1P2HumidifierOnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x56EA | P1P2AntiFreezeControlOnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x56EB | P1P2FloatOnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x56EC | P1P2T1T2OnOffUnit8 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x56ED | P1P2IndoorSuctionAirThermistorUnit8 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x56EE | P1P2IndoorUnitHeatExchangerThermistorUnit8 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x56EF | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit8 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x56F0 | P1P2IndoorUnitDischargeAirThermistorUnit8 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x56F1 | P1P2IndoorUnitOperatingTimeUnit8 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x56F2 | P1P2IndoorUnitFanOperationTimeUnit8 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x56F3 | P1P2IndoorUnitEnergizedTimeUnit8 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x56F4 | P1P2IndoorUnitAddressUnit8 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x56F5 | P1P2IndoorUnitModelNameManualUnit8 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x56F6 | P1P2IndoorUnitTypeUnit8 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x56F7 | P1P2IndoorUnitSerialNumberEquipUnit8 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #9 Status data
0x5700 | P1P2IndoorUnitDataValidUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5701 | P1P2IndoorUnitModelNameUnit9 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5702 | P1P2IndoorUnitSerialNumberUnit9 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5703 | P1P2IndoorUnitFanTapUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5704 | P1P2IndoorUnitFlapSwingUnit9 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5705 | P1P2IndoorUnitFanSpeedUnit9 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5706 | P1P2IndoorUnitEEVOpenPulsesUnit9 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5707 | P1P2DrainPumpOnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5708 | P1P2ElectricHeaterOnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5709 | P1P2HumidifierOnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x570A | P1P2AntiFreezeControlOnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x570B | P1P2FloatOnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x570C | P1P2T1T2OnOffUnit9 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x570D | P1P2IndoorSuctionAirThermistorUnit9 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x570E | P1P2IndoorUnitHeatExchangerThermistorUnit9 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x570F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit9 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5710 | P1P2IndoorUnitDischargeAirThermistorUnit9 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5711 | P1P2IndoorUnitOperatingTimeUnit9 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5712 | P1P2IndoorUnitFanOperationTimeUnit9 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5713 | P1P2IndoorUnitEnergizedTimeUnit9 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5714 | P1P2IndoorUnitAddressUnit9 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5715 | P1P2IndoorUnitModelNameManualUnit9 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5716 | P1P2IndoorUnitTypeUnit9 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5717 | P1P2IndoorUnitSerialNumberEquipUnit9 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #10 Status data
0x5720 | P1P2IndoorUnitDataValidUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5721 | P1P2IndoorUnitModelNameUnit10 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5722 | P1P2IndoorUnitSerialNumberUnit10 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5723 | P1P2IndoorUnitFanTapUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5724 | P1P2IndoorUnitFlapSwingUnit10 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5725 | P1P2IndoorUnitFanSpeedUnit10 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5726 | P1P2IndoorUnitEEVOpenPulsesUnit10 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5727 | P1P2DrainPumpOnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5728 | P1P2ElectricHeaterOnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5729 | P1P2HumidifierOnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x572A | P1P2AntiFreezeControlOnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x572B | P1P2FloatOnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x572C | P1P2T1T2OnOffUnit10 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x572D | P1P2IndoorSuctionAirThermistorUnit10 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x572E | P1P2IndoorUnitHeatExchangerThermistorUnit10 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x572F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit10 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5730 | P1P2IndoorUnitDischargeAirThermistorUnit10 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5731 | P1P2IndoorUnitOperatingTimeUnit10 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5732 | P1P2IndoorUnitFanOperationTimeUnit10 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5733 | P1P2IndoorUnitEnergizedTimeUnit10 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5734 | P1P2IndoorUnitAddressUnit10 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5735 | P1P2IndoorUnitModelNameManualUnit10 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5736 | P1P2IndoorUnitTypeUnit10 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5737 | P1P2IndoorUnitSerialNumberEquipUnit10 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #11 Status data
0x5740 | P1P2IndoorUnitDataValidUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5741 | P1P2IndoorUnitModelNameUnit11 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5742 | P1P2IndoorUnitSerialNumberUnit11 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5743 | P1P2IndoorUnitFanTapUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5744 | P1P2IndoorUnitFlapSwingUnit11 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5745 | P1P2IndoorUnitFanSpeedUnit11 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5746 | P1P2IndoorUnitEEVOpenPulsesUnit11 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5747 | P1P2DrainPumpOnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5748 | P1P2ElectricHeaterOnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5749 | P1P2HumidifierOnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x574A | P1P2AntiFreezeControlOnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x574B | P1P2FloatOnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x574C | P1P2T1T2OnOffUnit11 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x574D | P1P2IndoorSuctionAirThermistorUnit11 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x574E | P1P2IndoorUnitHeatExchangerThermistorUnit11 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x574F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit11 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5750 | P1P2IndoorUnitDischargeAirThermistorUnit11 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5751 | P1P2IndoorUnitOperatingTimeUnit11 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5752 | P1P2IndoorUnitFanOperationTimeUnit11 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5753 | P1P2IndoorUnitEnergizedTimeUnit11 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5754 | P1P2IndoorUnitAddressUnit11 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5755 | P1P2IndoorUnitModelNameManualUnit11 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5756 | P1P2IndoorUnitTypeUnit11 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5757 | P1P2IndoorUnitSerialNumberEquipUnit11 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #12 Status data
0x5760 | P1P2IndoorUnitDataValidUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5761 | P1P2IndoorUnitModelNameUnit12 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5762 | P1P2IndoorUnitSerialNumberUnit12 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5763 | P1P2IndoorUnitFanTapUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5764 | P1P2IndoorUnitFlapSwingUnit12 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5765 | P1P2IndoorUnitFanSpeedUnit12 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5766 | P1P2IndoorUnitEEVOpenPulsesUnit12 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5767 | P1P2DrainPumpOnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5768 | P1P2ElectricHeaterOnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5769 | P1P2HumidifierOnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x576A | P1P2AntiFreezeControlOnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x576B | P1P2FloatOnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x576C | P1P2T1T2OnOffUnit12 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x576D | P1P2IndoorSuctionAirThermistorUnit12 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x576E | P1P2IndoorUnitHeatExchangerThermistorUnit12 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x576F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit12 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5770 | P1P2IndoorUnitDischargeAirThermistorUnit12 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5771 | P1P2IndoorUnitOperatingTimeUnit12 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5772 | P1P2IndoorUnitFanOperationTimeUnit12 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5773 | P1P2IndoorUnitEnergizedTimeUnit12 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5774 | P1P2IndoorUnitAddressUnit12 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5775 | P1P2IndoorUnitModelNameManualUnit12 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5776 | P1P2IndoorUnitTypeUnit12 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5777 | P1P2IndoorUnitSerialNumberEquipUnit12 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #13 Status data
0x5780 | P1P2IndoorUnitDataValidUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x5781 | P1P2IndoorUnitModelNameUnit13 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x5782 | P1P2IndoorUnitSerialNumberUnit13 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x5783 | P1P2IndoorUnitFanTapUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x5784 | P1P2IndoorUnitFlapSwingUnit13 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x5785 | P1P2IndoorUnitFanSpeedUnit13 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x5786 | P1P2IndoorUnitEEVOpenPulsesUnit13 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x5787 | P1P2DrainPumpOnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x5788 | P1P2ElectricHeaterOnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x5789 | P1P2HumidifierOnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x578A | P1P2AntiFreezeControlOnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x578B | P1P2FloatOnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x578C | P1P2T1T2OnOffUnit13 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x578D | P1P2IndoorSuctionAirThermistorUnit13 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x578E | P1P2IndoorUnitHeatExchangerThermistorUnit13 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x578F | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit13 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x5790 | P1P2IndoorUnitDischargeAirThermistorUnit13 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x5791 | P1P2IndoorUnitOperatingTimeUnit13 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x5792 | P1P2IndoorUnitFanOperationTimeUnit13 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x5793 | P1P2IndoorUnitEnergizedTimeUnit13 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x5794 | P1P2IndoorUnitAddressUnit13 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x5795 | P1P2IndoorUnitModelNameManualUnit13 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x5796 | P1P2IndoorUnitTypeUnit13 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x5797 | P1P2IndoorUnitSerialNumberEquipUnit13 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #14 Status data
0x57A0 | P1P2IndoorUnitDataValidUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x57A1 | P1P2IndoorUnitModelNameUnit14 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x57A2 | P1P2IndoorUnitSerialNumberUnit14 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x57A3 | P1P2IndoorUnitFanTapUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x57A4 | P1P2IndoorUnitFlapSwingUnit14 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x57A5 | P1P2IndoorUnitFanSpeedUnit14 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x57A6 | P1P2IndoorUnitEEVOpenPulsesUnit14 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x57A7 | P1P2DrainPumpOnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x57A8 | P1P2ElectricHeaterOnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x57A9 | P1P2HumidifierOnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x57AA | P1P2AntiFreezeControlOnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x57AB | P1P2FloatOnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x57AC | P1P2T1T2OnOffUnit14 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x57AD | P1P2IndoorSuctionAirThermistorUnit14 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x57AE | P1P2IndoorUnitHeatExchangerThermistorUnit14 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x57AF | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit14 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x57B0 | P1P2IndoorUnitDischargeAirThermistorUnit14 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x57B1 | P1P2IndoorUnitOperatingTimeUnit14 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x57B2 | P1P2IndoorUnitFanOperationTimeUnit14 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x57B3 | P1P2IndoorUnitEnergizedTimeUnit14 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x57B4 | P1P2IndoorUnitAddressUnit14 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x57B5 | P1P2IndoorUnitModelNameManualUnit14 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x57B6 | P1P2IndoorUnitTypeUnit14 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x57B7 | P1P2IndoorUnitSerialNumberEquipUnit14 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//P1P2 (VRV) Indoor Unit #15 Status data
0x57C0 | P1P2IndoorUnitDataValidUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | NOT USED; 0: invalid 1: valid
0x57C1 | P1P2IndoorUnitModelNameUnit15 | CHAR | 0 | 20 | NULL | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number; may be reported by some VRV units.
0x57C2 | P1P2IndoorUnitSerialNumberUnit15 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, for manual entry by UI since not reported by VRV units.
0x57C3 | P1P2IndoorUnitFanTapUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: No fan rotation; 1: Fan rotation exists (OPCB4 D[2])
0x57C4 | P1P2IndoorUnitFlapSwingUnit15 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | bit0-3, fan direction: 0-4=positions 1-5, 5=Wireless Stop, 6=stop, 7=oscillate, 10=airflow blocked; bit4-7, fan airflow (OPCB4 D[1]): 0=off, 1=extra low, 2=low, 3=medium, 4=high, 5=extra high, 6=medium low, 7=medium high;
0x57C5 | P1P2IndoorUnitFanSpeedUnit15 | UINT8 | 0 | 0xFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Fan speed (rpm) (value is divided by 10) (OPCB4 D[3])
0x57C6 | P1P2IndoorUnitEEVOpenPulsesUnit15 | UINT16 | 0 | 9999 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | upper byte (OPCB4 D[4])
0x57C7 | P1P2DrainPumpOnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit0)
0x57C8 | P1P2ElectricHeaterOnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit1)
0x57C9 | P1P2HumidifierOnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit2)
0x57CA | P1P2AntiFreezeControlOnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit4)
0x57CB | P1P2FloatOnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit6)
0x57CC | P1P2T1T2OnOffUnit15 | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: OFF 1: ON (OPCB4 D[0] bit7)
0x57CD | P1P2IndoorSuctionAirThermistorUnit15 | FLOAT | -255 | 255 | 255 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Suction air thermistor temperature in Celsius; Used as control temperature when "tempHumControlSource" is set to a '1' by writing this return air temperature to "tempIndoor", which is then sent by the P1P2 PIC24 code to the IDU for control.
0x57CE | P1P2IndoorUnitHeatExchangerThermistorUnit15 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger thermistor temperature in Celsius
0x57CF | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit15 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU heat exchanger gas pipe thermistor temperature
0x57D0 | P1P2IndoorUnitDischargeAirThermistorUnit15 | FLOAT | -255 | 255 | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU discharge air thermistor temperature in Celsius
0x57D1 | P1P2IndoorUnitOperatingTimeUnit15 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | IDU operating time
0x57D2 | P1P2IndoorUnitFanOperationTimeUnit15 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit fan operating time
0x57D3 | P1P2IndoorUnitEnergizedTimeUnit15 | UINT16 | 0 | 0xFFFF | 0 | FALSE | READ | READWRITE | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit energized time
0x57D4 | P1P2IndoorUnitAddressUnit15 | UINT8 | 0 | 0xFF | 0 | FALSE | READWRITE | READWRITE | READWRITE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | Indoor unit D3 address;
0x57D5 | P1P2IndoorUnitModelNameManualUnit15 | CHAR | 0 | 20 | NULL | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII model number, manually entered by installer and used in place of model number from equipment in "P1P2IndoorUnitModelNameUnit1" since that variable is not usually populated.
0x57D6 | P1P2IndoorUnitTypeUnit15 | UINT8 | 0 | 4,0xFF | 0xFF | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: wall-mount unit; 1: ceiling cassette; 2: single-flow cassette; 3: floor-mount unit; 4: concealed ceiling unit; 0xFF: no selection (used to display louver direction settings FOR P1P2);
0x57D7 | P1P2IndoorUnitSerialNumberEquipUnit15 | CHAR | 0 | 20 | NULL | TRUE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | ASCII, from IDU, though most or all VRV units don't report this.
//Data valid bits, P1P2 (VRV) Indoor Unit #1 Status data
0x5800 | P1P2IndoorUnitSerialNumberEquipUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5801 | P1P2IndoorUnitModelNameUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5802 | P1P2IndoorUnitFanTapUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5803 | P1P2IndoorUnitFlapSwingUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5804 | P1P2IndoorUnitFanSpeedUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5805 | P1P2IndoorUnitEEVOpenPulsesUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5806 | P1P2DrainPumpOnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5807 | P1P2ElectricHeaterOnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5808 | P1P2HumidifierOnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5809 | P1P2AntiFreezeControlOnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580A | P1P2FloatOnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580B | P1P2T1T2OnOffUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580C | P1P2IndoorSuctionAirThermistorUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580D | P1P2IndoorUnitHeatExchangerThermistorUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x580F | P1P2IndoorUnitDischargeAirThermistorUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5810 | P1P2IndoorUnitOperatingTimeUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5811 | P1P2IndoorUnitFanOperationTimeUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5812 | P1P2IndoorUnitEnergizedTimeUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5813 | P1P2IndoorUnitAddressUnit1Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #2 Status data
0x5900 | P1P2IndoorUnitSerialNumberEquipUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5901 | P1P2IndoorUnitModelNameUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5902 | P1P2IndoorUnitFanTapUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5903 | P1P2IndoorUnitFlapSwingUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5904 | P1P2IndoorUnitFanSpeedUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5905 | P1P2IndoorUnitEEVOpenPulsesUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5906 | P1P2DrainPumpOnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5907 | P1P2ElectricHeaterOnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5908 | P1P2HumidifierOnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5909 | P1P2AntiFreezeControlOnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590A | P1P2FloatOnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590B | P1P2T1T2OnOffUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590C | P1P2IndoorSuctionAirThermistorUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590D | P1P2IndoorUnitHeatExchangerThermistorUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x590F | P1P2IndoorUnitDischargeAirThermistorUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5910 | P1P2IndoorUnitOperatingTimeUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5911 | P1P2IndoorUnitFanOperationTimeUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5912 | P1P2IndoorUnitEnergizedTimeUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5913 | P1P2IndoorUnitAddressUnit2Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #3 Status data
0x5A00 | P1P2IndoorUnitSerialNumberEquipUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A01 | P1P2IndoorUnitModelNameUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A02 | P1P2IndoorUnitFanTapUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A03 | P1P2IndoorUnitFlapSwingUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A04 | P1P2IndoorUnitFanSpeedUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A05 | P1P2IndoorUnitEEVOpenPulsesUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A06 | P1P2DrainPumpOnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A07 | P1P2ElectricHeaterOnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A08 | P1P2HumidifierOnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A09 | P1P2AntiFreezeControlOnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0A | P1P2FloatOnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0B | P1P2T1T2OnOffUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0C | P1P2IndoorSuctionAirThermistorUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0D | P1P2IndoorUnitHeatExchangerThermistorUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A0F | P1P2IndoorUnitDischargeAirThermistorUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A10 | P1P2IndoorUnitOperatingTimeUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A11 | P1P2IndoorUnitFanOperationTimeUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A12 | P1P2IndoorUnitEnergizedTimeUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5A13 | P1P2IndoorUnitAddressUnit3Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #4 Status data
0x5B00 | P1P2IndoorUnitSerialNumberEquipUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B01 | P1P2IndoorUnitModelNameUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B02 | P1P2IndoorUnitFanTapUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B03 | P1P2IndoorUnitFlapSwingUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B04 | P1P2IndoorUnitFanSpeedUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B05 | P1P2IndoorUnitEEVOpenPulsesUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B06 | P1P2DrainPumpOnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B07 | P1P2ElectricHeaterOnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B08 | P1P2HumidifierOnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B09 | P1P2AntiFreezeControlOnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0A | P1P2FloatOnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0B | P1P2T1T2OnOffUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0C | P1P2IndoorSuctionAirThermistorUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0D | P1P2IndoorUnitHeatExchangerThermistorUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B0F | P1P2IndoorUnitDischargeAirThermistorUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B10 | P1P2IndoorUnitOperatingTimeUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B11 | P1P2IndoorUnitFanOperationTimeUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B12 | P1P2IndoorUnitEnergizedTimeUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5B13 | P1P2IndoorUnitAddressUnit4Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #5 Status data
0x5C00 | P1P2IndoorUnitSerialNumberEquipUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C01 | P1P2IndoorUnitModelNameUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C02 | P1P2IndoorUnitFanTapUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C03 | P1P2IndoorUnitFlapSwingUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C04 | P1P2IndoorUnitFanSpeedUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C05 | P1P2IndoorUnitEEVOpenPulsesUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C06 | P1P2DrainPumpOnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C07 | P1P2ElectricHeaterOnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C08 | P1P2HumidifierOnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C09 | P1P2AntiFreezeControlOnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0A | P1P2FloatOnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0B | P1P2T1T2OnOffUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0C | P1P2IndoorSuctionAirThermistorUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0D | P1P2IndoorUnitHeatExchangerThermistorUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C0F | P1P2IndoorUnitDischargeAirThermistorUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C10 | P1P2IndoorUnitOperatingTimeUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C11 | P1P2IndoorUnitFanOperationTimeUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C12 | P1P2IndoorUnitEnergizedTimeUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5C13 | P1P2IndoorUnitAddressUnit5Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #6 Status data
0x5D00 | P1P2IndoorUnitSerialNumberEquipUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D01 | P1P2IndoorUnitModelNameUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D02 | P1P2IndoorUnitFanTapUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D03 | P1P2IndoorUnitFlapSwingUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D04 | P1P2IndoorUnitFanSpeedUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D05 | P1P2IndoorUnitEEVOpenPulsesUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D06 | P1P2DrainPumpOnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D07 | P1P2ElectricHeaterOnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D08 | P1P2HumidifierOnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D09 | P1P2AntiFreezeControlOnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0A | P1P2FloatOnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0B | P1P2T1T2OnOffUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0C | P1P2IndoorSuctionAirThermistorUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0D | P1P2IndoorUnitHeatExchangerThermistorUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D0F | P1P2IndoorUnitDischargeAirThermistorUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D10 | P1P2IndoorUnitOperatingTimeUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D11 | P1P2IndoorUnitFanOperationTimeUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D12 | P1P2IndoorUnitEnergizedTimeUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5D13 | P1P2IndoorUnitAddressUnit6Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #7 Status data
0x5E00 | P1P2IndoorUnitSerialNumberEquipUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E01 | P1P2IndoorUnitModelNameUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E02 | P1P2IndoorUnitFanTapUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E03 | P1P2IndoorUnitFlapSwingUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E04 | P1P2IndoorUnitFanSpeedUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E05 | P1P2IndoorUnitEEVOpenPulsesUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E06 | P1P2DrainPumpOnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E07 | P1P2ElectricHeaterOnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E08 | P1P2HumidifierOnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E09 | P1P2AntiFreezeControlOnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0A | P1P2FloatOnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0B | P1P2T1T2OnOffUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0C | P1P2IndoorSuctionAirThermistorUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0D | P1P2IndoorUnitHeatExchangerThermistorUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E0F | P1P2IndoorUnitDischargeAirThermistorUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E10 | P1P2IndoorUnitOperatingTimeUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E11 | P1P2IndoorUnitFanOperationTimeUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E12 | P1P2IndoorUnitEnergizedTimeUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5E13 | P1P2IndoorUnitAddressUnit7Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #8 Status data
0x5F00 | P1P2IndoorUnitSerialNumberEquipUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F01 | P1P2IndoorUnitModelNameUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F02 | P1P2IndoorUnitFanTapUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F03 | P1P2IndoorUnitFlapSwingUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F04 | P1P2IndoorUnitFanSpeedUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F05 | P1P2IndoorUnitEEVOpenPulsesUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F06 | P1P2DrainPumpOnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F07 | P1P2ElectricHeaterOnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F08 | P1P2HumidifierOnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F09 | P1P2AntiFreezeControlOnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0A | P1P2FloatOnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0B | P1P2T1T2OnOffUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0C | P1P2IndoorSuctionAirThermistorUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0D | P1P2IndoorUnitHeatExchangerThermistorUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F0F | P1P2IndoorUnitDischargeAirThermistorUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F10 | P1P2IndoorUnitOperatingTimeUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F11 | P1P2IndoorUnitFanOperationTimeUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F12 | P1P2IndoorUnitEnergizedTimeUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x5F13 | P1P2IndoorUnitAddressUnit8Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//CoProcessor State
0x6000 | coProcessorUpdating | BIT | 0 | 1 | 0 | FALSE | READ | READ | READ | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | CoProcessor is being programmed
//Data valid bits, P1P2 (VRV) Indoor Unit #9 Status data
0x6100 | P1P2IndoorUnitSerialNumberEquipUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6101 | P1P2IndoorUnitModelNameUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6102 | P1P2IndoorUnitFanTapUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6103 | P1P2IndoorUnitFlapSwingUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6104 | P1P2IndoorUnitFanSpeedUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6105 | P1P2IndoorUnitEEVOpenPulsesUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6106 | P1P2DrainPumpOnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6107 | P1P2ElectricHeaterOnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6108 | P1P2HumidifierOnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6109 | P1P2AntiFreezeControlOnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610A | P1P2FloatOnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610B | P1P2T1T2OnOffUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610C | P1P2IndoorSuctionAirThermistorUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610D | P1P2IndoorUnitHeatExchangerThermistorUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x610F | P1P2IndoorUnitDischargeAirThermistorUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6110 | P1P2IndoorUnitOperatingTimeUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6111 | P1P2IndoorUnitFanOperationTimeUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6112 | P1P2IndoorUnitEnergizedTimeUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6113 | P1P2IndoorUnitAddressUnit9Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #10 Status data
0x6200 | P1P2IndoorUnitSerialNumberEquipUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6201 | P1P2IndoorUnitModelNameUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6202 | P1P2IndoorUnitFanTapUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6203 | P1P2IndoorUnitFlapSwingUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6204 | P1P2IndoorUnitFanSpeedUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6205 | P1P2IndoorUnitEEVOpenPulsesUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6206 | P1P2DrainPumpOnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6207 | P1P2ElectricHeaterOnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6208 | P1P2HumidifierOnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6209 | P1P2AntiFreezeControlOnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620A | P1P2FloatOnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620B | P1P2T1T2OnOffUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620C | P1P2IndoorSuctionAirThermistorUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620D | P1P2IndoorUnitHeatExchangerThermistorUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x620F | P1P2IndoorUnitDischargeAirThermistorUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6210 | P1P2IndoorUnitOperatingTimeUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6211 | P1P2IndoorUnitFanOperationTimeUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6212 | P1P2IndoorUnitEnergizedTimeUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6213 | P1P2IndoorUnitAddressUnit10Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #11 Status data
0x6300 | P1P2IndoorUnitSerialNumberEquipUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6301 | P1P2IndoorUnitModelNameUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6302 | P1P2IndoorUnitFanTapUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6303 | P1P2IndoorUnitFlapSwingUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6304 | P1P2IndoorUnitFanSpeedUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6305 | P1P2IndoorUnitEEVOpenPulsesUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6306 | P1P2DrainPumpOnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6307 | P1P2ElectricHeaterOnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6308 | P1P2HumidifierOnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6309 | P1P2AntiFreezeControlOnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630A | P1P2FloatOnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630B | P1P2T1T2OnOffUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630C | P1P2IndoorSuctionAirThermistorUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630D | P1P2IndoorUnitHeatExchangerThermistorUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x630F | P1P2IndoorUnitDischargeAirThermistorUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6310 | P1P2IndoorUnitOperatingTimeUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6311 | P1P2IndoorUnitFanOperationTimeUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6312 | P1P2IndoorUnitEnergizedTimeUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6313 | P1P2IndoorUnitAddressUnit11Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #12 Status data
0x6400 | P1P2IndoorUnitSerialNumberEquipUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6401 | P1P2IndoorUnitModelNameUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6402 | P1P2IndoorUnitFanTapUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6403 | P1P2IndoorUnitFlapSwingUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6404 | P1P2IndoorUnitFanSpeedUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6405 | P1P2IndoorUnitEEVOpenPulsesUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6406 | P1P2DrainPumpOnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6407 | P1P2ElectricHeaterOnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6408 | P1P2HumidifierOnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6409 | P1P2AntiFreezeControlOnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640A | P1P2FloatOnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640B | P1P2T1T2OnOffUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640C | P1P2IndoorSuctionAirThermistorUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640D | P1P2IndoorUnitHeatExchangerThermistorUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x640F | P1P2IndoorUnitDischargeAirThermistorUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6410 | P1P2IndoorUnitOperatingTimeUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6411 | P1P2IndoorUnitFanOperationTimeUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6412 | P1P2IndoorUnitEnergizedTimeUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6413 | P1P2IndoorUnitAddressUnit12Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #13 Status data
0x6500 | P1P2IndoorUnitSerialNumberEquipUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6501 | P1P2IndoorUnitModelNameUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6502 | P1P2IndoorUnitFanTapUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6503 | P1P2IndoorUnitFlapSwingUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6504 | P1P2IndoorUnitFanSpeedUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6505 | P1P2IndoorUnitEEVOpenPulsesUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6506 | P1P2DrainPumpOnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6507 | P1P2ElectricHeaterOnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6508 | P1P2HumidifierOnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6509 | P1P2AntiFreezeControlOnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650A | P1P2FloatOnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650B | P1P2T1T2OnOffUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650C | P1P2IndoorSuctionAirThermistorUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650D | P1P2IndoorUnitHeatExchangerThermistorUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x650F | P1P2IndoorUnitDischargeAirThermistorUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6510 | P1P2IndoorUnitOperatingTimeUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6511 | P1P2IndoorUnitFanOperationTimeUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6512 | P1P2IndoorUnitEnergizedTimeUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6513 | P1P2IndoorUnitAddressUnit13Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #14 Status data
0x6600 | P1P2IndoorUnitSerialNumberEquipUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6601 | P1P2IndoorUnitModelNameUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6602 | P1P2IndoorUnitFanTapUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6603 | P1P2IndoorUnitFlapSwingUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6604 | P1P2IndoorUnitFanSpeedUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6605 | P1P2IndoorUnitEEVOpenPulsesUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6606 | P1P2DrainPumpOnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6607 | P1P2ElectricHeaterOnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6608 | P1P2HumidifierOnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6609 | P1P2AntiFreezeControlOnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660A | P1P2FloatOnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660B | P1P2T1T2OnOffUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660C | P1P2IndoorSuctionAirThermistorUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660D | P1P2IndoorUnitHeatExchangerThermistorUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x660F | P1P2IndoorUnitDischargeAirThermistorUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6610 | P1P2IndoorUnitOperatingTimeUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6611 | P1P2IndoorUnitFanOperationTimeUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6612 | P1P2IndoorUnitEnergizedTimeUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6613 | P1P2IndoorUnitAddressUnit14Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//Data valid bits, P1P2 (VRV) Indoor Unit #15 Status data
0x6700 | P1P2IndoorUnitSerialNumberEquipUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6701 | P1P2IndoorUnitModelNameUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6702 | P1P2IndoorUnitFanTapUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6703 | P1P2IndoorUnitFlapSwingUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6704 | P1P2IndoorUnitFanSpeedUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6705 | P1P2IndoorUnitEEVOpenPulsesUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6706 | P1P2DrainPumpOnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6707 | P1P2ElectricHeaterOnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6708 | P1P2HumidifierOnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6709 | P1P2AntiFreezeControlOnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670A | P1P2FloatOnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670B | P1P2T1T2OnOffUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670C | P1P2IndoorSuctionAirThermistorUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670D | P1P2IndoorUnitHeatExchangerThermistorUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670E | P1P2IndoorUnitHeatExchangerGasPipeThermistorUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x670F | P1P2IndoorUnitDischargeAirThermistorUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6710 | P1P2IndoorUnitOperatingTimeUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6711 | P1P2IndoorUnitFanOperationTimeUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6712 | P1P2IndoorUnitEnergizedTimeUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
0x6713 | P1P2IndoorUnitAddressUnit15Valid | BIT | 0 | 1 | 0 | FALSE | READ | READWRITE | READ | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | 0: invalid 1: valid
//HEMS global variables
0x8000 | HEMSsetbackEnable | BIT | 0 | 1 | 1 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=disabled; 1=enabled;
0x8001 | HEMSsetbackOnGrid | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=disabled; 1=enabled; setback temperatures when on grid, set by end-user;
0x8002 | HEMSsetbackOffgrid | INT8 | 0 | 2, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=no setback; 1=energy savings; 2=off mode, setback behavior when off grid, set by end-user;
0x8003 | HEMSsetbackLevel1 | INT8 | 0 | 100, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase battery level in % for 1st setback level; battery percent to limit to 70% compressor
0x8004 | HEMSsetbackLevel2 | INT8 | 0 | 100, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase battery level in % for 2nd setback level; battery percent to limit to 40% compressor
0x8005 | HEMSsetbackLevel3 | INT8 | 0 | 100, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase battery level in % for 3rd setback level; battery percent to turn compressor off;
//Enphase global variables
0x8030 | EnphaseUsername | CHAR | 0 | 24 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy user name
0x8031 | EnphasePassword | CHAR | 0 | 24 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy password
0x8032 | EnphaseEnable | BIT | 0 | 1 | 0 | TRUE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=disabled; 1=enabled;
//Enphase System 1 variables
0x8040 | Enphase1EnvoySerial | CHAR | 0 | 16 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy Serial Number, eg. 202348029160
0x8041 | Enphase1EnvoyIP | CHAR | 0 | 16 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy IP number
0x8042 | Enphase1EnvoyOnline | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=offline; 1=online;
//Enphase System 1 status variables
0x8050 | Enphase1IsOnGrid | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=Enphase off grid; 1=Enphase on grid
0x8051 | Enphase1BatteryLevelNow | INT8 | 0 | 100, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase battery level in %;
0x8052 | Enphase1SolarNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase solar power now, eg 9106.109
0x8053 | Enphase1SolarState | INT8 | 0 | 1, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=generating; Solar state
0x8054 | Enphase1StorageNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase storage now; eg 9106.109
0x8055 | Enphase1StorageState | INT8 | 0 | 2, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=charging; 2=discharging; Enphase storage state
0x8056 | Enphase1GridNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase grid now; eg 9106.109
0x8057 | Enphase1GridState | INT8 | 0 | 2, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=importing; 2=exporting;
0x8058 | Enphase1LoadNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase load now; eg 9106.109
0x8059 | Enphase1LoadState | INT8 | 0 | 1, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=consuming; Load state
0x805A | Enphase1PowerSource | INT8 | 0 | 15, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | bit 0=off; bit 1=grid; bit 2=solar; bit 3=battery; power source(s) currently used;
//Enphase System 2 variables
0x8060 | Enphase2EnvoySerial | CHAR | 0 | 16 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy Serial Number, eg. 202348029160
0x8061 | Enphase2EnvoyIP | CHAR | 0 | 16 | NULL | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Envoy IP number
0x8062 | Enphase2EnvoyOnline | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=offline; 1=online;
//Enphase System 2 variables
0x8070 | Enphase2IsOnGrid | BIT | 0 | 1 | 0 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=Enphase off grid; 1=Enphase on grid
0x8071 | Enphase2BatteryLevelNow | INT8 | 0 | 100, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase battery level in %;
0x8072 | Enphase2SolarNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase solar power now, eg 9106.109
0x8073 | Enphase2SolarState | INT8 | 0 | 1, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=generating; Solar state
0x8074 | Enphase2StorageNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase storage now; eg 9106.109
0x8075 | Enphase2StorageState | INT8 | 0 | 2, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=charging; 2=discharging; Enphase storage state
0x8076 | Enphase2GridNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase grid now; eg 9106.109
0x8077 | Enphase2GridState | INT8 | 0 | 2, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=importing; 2=exporting;
0x8078 | Enphase2LoadNow | FLOAT | 0 | 255 | 255 | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | Enphase load now; eg 9106.109
0x8079 | Enphase2LoadState | INT8 | 0 | 1, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 0=idle; 1=consuming; Load state
0x807A | Enphase2PowerSource | INT8 | 0 | 15, 0x7F | 0x7F | FALSE | READWRITE | READ | READWRITE | TRUE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | bit 0=off; bit 1=grid; bit 2=solar; bit 3=battery; power source(s) currently used;
//Zone Board OTA update variables
0xF000 | ZBBulkDataPack0 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF001 | ZBBulkDataPack1 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF002 | ZBBulkDataPack2 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF003 | ZBBulkDataPack3 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF004 | ZBBulkDataPack4 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF005 | ZBBulkDataPack5 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF006 | ZBBulkDataPack6 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF007 | ZBBulkDataPack7 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF008 | ZBBulkDataPack8 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF009 | ZBBulkDataPack9 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00A | ZBBulkDataPack10 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00B | ZBBulkDataPack11 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00C | ZBBulkDataPack12 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00D | ZBBulkDataPack13 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00E | ZBBulkDataPack14 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF00F | ZBBulkDataPack15 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF010 | ZBBulkDataPack16 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF011 | ZBBulkDataPack17 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF012 | ZBBulkDataPack18 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF013 | ZBBulkDataPack19 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF014 | ZBBulkDataPack20 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF015 | ZBBulkDataPack21 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF016 | ZBBulkDataPack22 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF017 | ZBBulkDataPack23 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF018 | ZBBulkDataPack24 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF019 | ZBBulkDataPack25 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01A | ZBBulkDataPack26 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01B | ZBBulkDataPack27 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01C | ZBBulkDataPack28 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01D | ZBBulkDataPack29 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01E | ZBBulkDataPack30 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF01F | ZBBulkDataPack31 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF020 | ZBBulkDataPack32 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF021 | ZBBulkDataPack33 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF022 | ZBBulkDataPack34 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF023 | ZBBulkDataPack35 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF024 | ZBBulkDataPack36 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF025 | ZBBulkDataPack37 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF026 | ZBBulkDataPack38 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF027 | ZBBulkDataPack39 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF028 | ZBBulkDataPack40 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF029 | ZBBulkDataPack41 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02A | ZBBulkDataPack42 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02B | ZBBulkDataPack43 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02C | ZBBulkDataPack44 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02D | ZBBulkDataPack45 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02E | ZBBulkDataPack46 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF02F | ZBBulkDataPack47 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF030 | ZBBulkDataPack48 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF031 | ZBBulkDataPack49 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF032 | ZBBulkDataPack50 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF033 | ZBBulkDataPack51 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF034 | ZBBulkDataPack52 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF035 | ZBBulkDataPack53 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF036 | ZBBulkDataPack54 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF037 | ZBBulkDataPack55 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF038 | ZBBulkDataPack56 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF039 | ZBBulkDataPack57 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03A | ZBBulkDataPack58 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03B | ZBBulkDataPack59 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03C | ZBBulkDataPack60 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03D | ZBBulkDataPack61 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03E | ZBBulkDataPack62 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board
0xF03F | ZBBulkDataPack63 | CHAR | 0 | 240 | NULL | FALSE | NONE | READ | NONE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | 240 byte buffer to transfer software update to zone board